## SECTION-B
Ser No | Description of Work | Unit | No of Units required | Unit Rate to be quoted by contractor in figures and words in Rs. | Amount
1 | 2 | 4 | 5
1 | Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, Aluminium bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required.(MNS officer's Mess) | Each | 01
INCOMER : 1 No.100 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & Fixed magnetic releases.
BUS BARS : 200 Amps. TP&N aluminium bus bars (25 KA Ics).
OUT GOINGS 6 Nos. 25A 4P, MCB (10KA). Space for 2 Nos.25A 4P, MCB
2 | All as per Srl item 01 above but following mountings. (Servant quarters for Capt & Below of 12) INCOMER : 1 No.40 Amps. 4P MCB(10 KA). BUS BARS : 63 Amps. TP&N aluminium bus bars. | Each | 01
OUT GOINGS
Space for 12 Nos. Single phase electronic meters
13 Nos. 6A DP MCB (10KA).
Page total c/o summary
3 | All as per Srl item 01 above but following mountings.(single accn for Captain and below of 8 T/S) INCOMER : 1 No.80 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & Fixed magnetic releases. BUS BARS : 200 Amps. TP&N aluminium bus bars (25 KA Ics). | Each | 02
OUT GOINGS:-
Space for 8 Nos. Single phase electronic meters
8 Nos. 25A DP, MCB (10KA).
1 Nos. 6A DP, MCB (10KA).
4 | All as per Srl item 01 hereinbefore but following mountings. (Single JCO) INCOMER : 1 No.40 Amps. 4P MCB(10 KA). BUS BARS : 63 Amps. TP&N aluminium bus bars. OUT GOINGS :- | Each | 02
Space for 4 Nos. Single phase electronic meters
4 Nos. 20A DP, MCB (10KA).
1 No. 16A DP MCB (10KA).
1 Nos. 6A DP MCB (10KA).
5 | All as per Srl item 01 hereinbefore but following mountings.(SM barracks for 150 Hav& 230 OR's). INCOMER : 1 No.125 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & Fixed magnetic releases. BUS BARS : 200 Amps. TP&N aluminium bus bars (25 KA Ics). | Each | 02
OUT GOINGS : 8 Nos. 25A 4P, MCB (10KA).
6 | All as per Srl item 01 hereinbefore but following mountings.(single Accn for Major and md accn for non combats). INCOMER : 1 No.40 Amps. 4P MCB(10 KA). BUS BARS : 100 Amps. TP&N aluminium bus bars. | Each | 02
OUT GOINGS:-
Space for 4 Nos. Single phase electronic meters
4 Nos. 25A DP, MCB (10KA).
1 Nos. 6A DP MCB (10KA).
Page total c/o summary
7 | All as per Srl item 01 hereinbefore but following mountings.(servant quarters and garage for Major). INCOMER : 1 No.25 Amps. DP MCB(10 KA). BUS BARS : 63 Amps. SP&N aluminium bus bars. | Each | 01
OUT GOINGS:-
Space for 3 Nos. Single phase electronic meters
4 Nos. 6A DP, MCB (10KA).
8 | All as per Srl item 01 hereinbefore but following mountings.(MD accn for JCO). INCOMER : 1 No.63 Amps. 4P MCB(10 KA). BUS BARS : 100 Amps. TP&N aluminium bus bars. | Each | 01
OUT GOINGS:-
Space for 6 Nos. three phase electronic meters
6 Nos. 25A 4P, MCB (10KA).
1 Nos. 6A DP MCB (10KA).
9 | All as per Srl item 01 hereinbefore but following mountings.(MD accn for ORS). INCOMER :1 No.63 Amps. 4P MCB(10 KA) BUS BARS : 100 Amps. TP&N aluminium bus bars | Each | 03
OUT GOINGS:-
Space for 6 Nos. Single phase electronic meters
6 Nos. 25A DP, MCB (10KA).
1 Nos. 6A DP MCB (10KA).
10 | All as per Srl item 01 hereinbefore but following mountings.(welfare amenity). INCOMER : 1 No.100 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & Fixed magnetic releases. BUS BARS : 200 Amps. TP&N aluminium bus bars (25 KA Ics). | Each | 01
OUT GOINGS:-
4 Nos. 25A 4P, MCB (10KA).
4 Nos. 16A 4P, MCB (10KA).
Space for 2 Nos.25A 4P, MCB
Page total c/o summary
11 | All as per Srl item 01 hereinbefore but following mountings.(servant quarters for block of 4). INCOMER : 1 No.100 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & Fixed magnetic releases. BUS BARS : 200 Amps. TP&N aluminium bus bars (25 KA Ics). | Each | 01
OUT GOINGS:-
Space for 4 Nos. Single phase electronic meters
5 Nos. 6A DP, MCB (10KA).
Hospital Building
12 | All as per Srl item 01 hereinbefore but following mountings.(Major to Brigadier). INCOMER : 1 No.100 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & Fixed magnetic releases. BUS BARS : 200 Amps. TP&N aluminium bus bars (25 KA Ics). | Each | 02
OUT GOINGS:-
Space for 4 Nos. three phase electronic meters
4 Nos. 25A 4P, MCB (10KA).
1 Nos. 6A DP MCB (10KA).
13 | Supply only 1000 mm wide and 6mm thick corrugated insulation rubber matting suitable for 1100 volts grade. | RM | 50
Page total c/o summary
Earthing
14 | Maintenance free earthing of make Electrolytic Earthing comprising of type 'K' copper 2.4 mm wall thickness, hollow tube 12 feet long, 2.125 inches outer diameter completely filled with non hazardous metallic salts (Tettafill) to achieve an earth resistance of less than 1 ohms and connected to earthing test point all as specified or indicated including testing on completion. | Each | 35
RISING MAINS, CABLE TRAY & LT CABLES(for Sub mains /Main)
Compact Sandwich Copper Rising mains
15 | Supply, Fixing ,inspection, handling, shifting, assembling, installation in correct assigned position of compact Sandwich construction copper rising mains (distribution bus trunking) and making proper connections, testing and commissioning 4 pole raising mains of copper bus bars with tap off connection points at every 1000mm intervals, expansion joints, fire barriers incl necessary support and louvers for ventilation, fabricated including 2 nos.of 50x6mm copper earthing conductor through out the length of the rising mains ( phase sequence should be matched with the incoming breaker provided at LT Panel ). Thrust pad shall be provided for each rising main for necessary support to rising main and to prevent the bus bar expansion in downward direction with end cover to close the end of rising main and to provode extra supports to bus bars at end, of following rating :-
(a) | Compact Sandwich Copper Rising mains Distribution Bus Trunking, rating 400A with short circuit withstand of 35 KA –1 sec,enclosure of GI Powder Coated RAL 7032 of sheet thickness 1.6mm ,with plug in point provison for each floor ,Class F insulation of three layer of polyester and ond one layer of glass mica IP – 54 protection ,one spring hanger/rigid hanger at each floor, temp rise of 55 Deg over an ambient of 40 Deg temperature. For RM-7,9,10,11,12 | RM | 96
Page total c/o summary
(b) | Compact Sandwich Copper Rising mains Distribution Bus Trunking, rating 630A with short circuit withstand of 40 KA –1 sec,enclosure of GI Powder Coated RAL 7032 of sheet thickness 1.6mm ,with plug in point provison for each floor ,Class F insulation of three layer of polyester and ond one layer of glass mica IP – 54 protection ,one spring hanger/rigid hanger at each floor, temp rise of 55 Deg over an ambient of 40 Deg temperature. For RM-4,6,8 | RM | 78
(c) | Compact Sandwich Copper Rising mains Distribution Bus Trunking, rating 800A with short circuit withstand of 50 KA –1 sec,enclosure of GI Powder Coated RAL 7032 of sheet thickness 1.6mm ,with plug in point provison for each floor ,Class F insulation of three layer of polyester and ond one layer of glass mica IP – 54 protection ,one spring hanger/rigid hanger at each floor, temp rise of 55 Deg over an ambient of 40 Deg temperature. For RM-3,4,6,8 | RM | 52
(d) | Compact Sandwich Copper Rising mains Distribution Bus Trunking, rating 1600A with short circuit withstand of 50 KA –1 sec,enclosure of GI Powder Coated RAL 7032 of sheet thickness 1.6mm ,with plug in point provison for each floor ,Class F insulation of three layer of polyester and ond one layer of glass mica IP – 54 protection ,one spring hanger/rigid hanger at each floor, temp rise of 55 Deg over an ambient of 40 Deg temperature. For RM-1 | RM | 24
16 | Supply, Fixing ,inspection, handling, shifting, assembling, installation in correct assigned position and including making proper connections, testing and commissioning MCCB Adopter Boxes fabricated out of 16 gauge CRCA sheet steel in cubical formation, dust and vermin proof and coupled with Rising mains. Boxes shall be treated with anticrrossive process before powder coating as per specifications, 2 nos. earthing terminals shall be provided. Boxes shall be suitable for connecting of rising mains at top and aluminuum cables at bottom, of following rating :-
Page total c/o summary
| (a) 400 Amp TPN End Feed unit complete with provision of 400 amps , TPN, MCCB of 35 KA (Ics) | Each | 06
| (b) 630 Amp TPN End Feed unit complete with provision of 630 amps,TPN, MCCB of 40 KA (Ics) | Each | 03
| (c) 800 Amp TPN End Feed unit complete with provision of 800 amps,4P, MCCB of 50 kA (Ics) | Each | 02
| (d) 1600 Amp TPN End Feed unit complete with provision of 1600 amps,4P, ACB ,MDO,Microprocessor (with O/L,S/C,INST. E/F) Releases of 50 kA (Ics) | Each | 01
17 | Supply, Fixing ,inspection, handling, shifting, assembling, installation in correct assigned position and including making proper connections, testing and commissioning Tap off Boxes fabricated out of 16 gauge CRCA sheet steel in cubical formation, dust and vermin proof and mounted on the Rising mains. Boxes shall be treated with anticrrossive process before powder coating as per specifications, 2 nos. earthing terminals, including providing of following MCCB's as required with all accessories and adequate space shall be provided for cables terminations, of following rating.
| (a) Tap off /Plug in box complete with 63A Amp, TPN, MCCB of 25 kA (Ics) | Each | 03
Page total c/o summary
| (b) Tap off /Plug in box complete with 100A Amp, TPN, MCCB of 25 kA (Ics) | Each | 06
| (c) Tap off /Plug in box complete with 125A Amp, TPN, MCCB of 25 kA (Ics) | Each | 06
| (d) Tap off /Plug in box complete with 160A Amp, TPN, MCCB of 25 kA (Ics) | Each | 13
| (e) Tap off /Plug in box complete with 200A Amp, TPN, MCCB of 25 kA (Ics) | Each | 12
| (f) Tap off /Plug in box complete with 250A Amp, TPN, MCCB of 35 kA (Ics) | Each | 02
| (g) Tap off /Plug in box complete with 300A Amp, TPN, MCCB of 35 kA (Ics) | Each | 04
| (h) Tap off /Plug in box complete with 400A Amp, TPN, MCCB of 35 kA (Ics) | Each | 01
Page total c/o summary
| (k) Tap off /Plug in box complete with 630A Amp, TPN, MCCB of 35 kA (Ics) | Each | 01
18 | Perforated type GI cable trays for supporting LT sub main cables fabricated from perforated 2mm thick MS CRCA sheet duly galvanised with expention coupler plates duly galvanised, with bolts washer and nuts. knock out hole cable connections as per approved design. including supporting steel, fish plates, fixing accessories, nut bolts, down rods, dash fastners complete as required. as per specifications, for following sizes :-
| (a) 150mm wide x 40mm x 40mm. | RM | 1800
| (b) 300mm wide x 40mm x 40mm. | RM | 3000
| (c) 450mm wide x 40mm x 40mm. | RM | 1200
| (d) 600mm wide x 40mm x 40mm. | RM | 500
| (e) 750mm wide x 40mm x 40mm. | RM | 200
Page total c/o summary
| (f) 1000mm wide x 40mm x 40mm. | RM | 150
19 | Supply, laying, testing and commissioning of 1.1 KV XLPE armoured / PVC insulated, PVC sheathed aluminium/copper conductor cables confirming to IS: 1554 part 1-1976 with latest amendment laid over existing Cable tray including clamping the cables to support, complete all as specified, of following sizes :-
| (a) 4 core x 25 sq.mm XLPE armoured, aluminium conductor cable | RM | 850
| (b) 3.5 core x 35 sq.mm XLPE armoured, aluminium conductor cable | RM | 200
| (c) 3.5c x 50 sq.mm XLPE armoured, aluminium conductor cable | RM | 350
| (d) 3.5 core x 70 sq.mm XLPE armoured, aluminium conductor cable | RM | 360
| (e) 3.5 core x 95 sq.mm XLPE armoured, aluminium conductor cable | RM | 600
Page total c/o summary
| (f) 3.5 core x 120 sq.mm XLPE armoured, aluminium conductor cable | RM | 500
| (g) 3.5 core x 150 sq.mm XLPE armoured, aluminium conductor cable | RM | 200
| (h) 3.5 core x 185 sq.mm XLPE armoured, aluminium conductor cable | RM | 50
| (j) 3.5 core x 240 sq.mm XLPE armoured, aluminium conductor cable | RM | 100
| (k) 3.5 core x 300 sq.mm XLPE armoured, aluminium conductor cable | RM | 150
| (l) 3.5 core x 400 sq.mm XLPE armoured, aluminium conductor cable | RM | 50
| (m) 4 core x 6 sq.mm armoured copper cable | RM | 13000
Page total c/o summary
| (n) 4 core x 10 sq.mm armoured copper cable | RM | 12000
| (o) 4 core x 16 sq.mm armoured copper cable | RM | 3200
| (p) 2 core x 10 sq.mm armoured copper cable | RM | 1600
20 | Cable end termination of 1.1 KV XLPE / PVC insulated, aluminium / copper conductor armoured cables, including supplying and fixing of crimping alumiinum/ copper lugs, double compression heavy duty glands with earthing facility at both ends of cables,including taping of cable leads with insulation tape etc ,complete all as specified, of following sizes :-
| (a) 4 core x 25 sq.mm XLPE armoured, aluminium conductor cable | Each | 80
| (b) 3.5 core x 35 sq.mm XLPE armoured, aluminium conductor cable | Each | 10
| (c) 3.5 core x 50 sq.mm XLPE armoured, aluminium conductor cable | Each | 10
Page total c/o summary
| (d) 3.5 core x 70 sq.mm XLPE armoured, aluminium conductor cable | Each | 10
| (e) 3.5 core x 95 sq.mm XLPE armoured, aluminium conductor cable | Each | 20
| (f) 3.5 core x 120 sq.mm XLPE armoured, aluminium conductor cable | Each | 16
| (g) 3.5 core x 150 sq.mm XLPE armoured, aluminium conductor cable | Each | 06
| (h) 3.5 core x 185 sq.mm XLPE armoured, aluminium conductor cable | Each | 04
| (j) 3.5 core x 240 sq.mm XLPE armoured, aluminium conductor cable | Each | 04
| (k) 3.5 core x 300 sq.mm XLPE armoured, aluminium conductor cable | Each | 04
Page total c/o summary
| (l) 3.5 core x 400 sq.mm XLPE armoured, aluminium conductor cable | Each | 04
| (m) 4 core x 6 sq.mm armoured copper cable | Each | 500
| (n) 4 core x 10 sq.mm armoured copper cable | Each | 400
| (o) 4 core x 16 sq.mm armoured copper cable | Each | 100
| (p) 2 core x 10 sq.mm armoured copper cable | Each | 100
21 | Supplying and drawing in existing conduit Wiring for TV outlet with coaxial cable double screened, aluminium. foiled, tinned copper ATC braid having an impedance of 75 Ohms and singal losses not more then 6 db etc as reqd. | RM | 2365
Page total c/o summary
ESDB-1,NSDB-2 (BASEMENT)
22 | Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, Aluminium bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 02
INCOMER : 1 No.63 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & Fixed magnetic releases.
INDICATING PANEL
(i) Voltmeter of range 0-500 volts with selector switch
(ii) Ammeter of range 0-60 Amps. with selector switch and required CT's.
(iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS :-
4 Nos. 25A 4P, MCB (10KA).TYPE-D
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection.
(b) Spare Space only for 2 Nos.25A 4P, MCB
Page total c/o summary
23 | NSDB-4(BASEMENT) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, Aluminium bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.100 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & Fixed magnetic releases.
INDICATING PANEL :- (i) Voltmeter of range 0-500 volts with selector switch (ii) Ammeter of range 0-100 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS :- 1 No. 25A 4P, MCB (10KA).TYPE-D. 3 Nos. 40A 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b)Spare Space only for 2 Nos.40A 4P, MCB.
Page total c/o summary
24 | ESDB-3(BASEMENT) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.63 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & Fixed magnetic releases.
INDICATING PANEL :- (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-60 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 5 Nos. 25A 4P, MCB (10KA).TYPE-D.
Note :(a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b)Spare Space only for 2 Nos.25A 4P, MCB.
Page total c/o summary
25 | ESDB-5(Ground FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, Aluminium bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.200 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & Fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-160 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS :- 5 Nos. 25A 4P, MCB (10KA).TYPE-D. 3 Nos. 40A 4P, MCB (10KA).TYPE-D. 2 Nos. 63A 4P, MCCB (25KA).
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.25A 4P, MCB.
Page total c/o summary
26 | NSDB-6(Ground FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.100 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & Fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-100 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS :- 2 Nos. 25A 4P, MCB (10KA).TYPE-D. 1 No. 40A 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b)Spare Space only for 2 Nos.40A 4P, MCB.
Page total c/o summary
27 | ESDB-7(Ground FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.630 Amps. 4P MCCB(35 KA Ics) with Adjustable thermal & Adjustable magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-600 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 800 Amps. TP&N Aluminium bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS :- 3 Nos. 25A 4P, MCB (10KA).TYPE-D. 3 Nos. 32A 4P, MCB (10KA).TYPE-D. 6 Nos. 40A 4P, MCB (10KA).TYPE-D. 3 Nos. 63A 4P, MCB (10KA).TYPE-D. 4 Nos. 63A 4P, MCCB (25KA).
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b)Spare Space only for 2 Nos.40A 4P, MCB.
Page total c/o summary
28 | NSDB-8(Ground FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.200 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & Fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-200 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 300 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 6 Nos. 40A 4P, MCB (10KA).
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.40A 4P, MCB.
Page total c/o summary
29 | ESDB-9(Ground FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, Aluminium bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.100 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & Fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-100 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 3 Nos. 25A 4P, MCB (10KA).TYPE-D. 3 Nos. 40A 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b)Spare Space only for 2 Nos.40A 4P, MCB.
Page total c/o summary
30 | NSDB-10(Ground FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.100 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & Fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-100 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 4 Nos. 25A 4P, MCB (10KA).TYPE-D. 1 No. 40A 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b)Spare Space only for 2 Nos.25A 4P, MCB.
Page total c/o summary
31 | ESDB-11(Ground FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.160 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & Fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-160 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 9 Nos. 25A 4P, MCB (10KA).TYPE-D, 1 No. 40A 4P, MCB (10KA).TYPE-D, 1 No. 63A 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b)Spare Space only for 2 Nos.25A 4P, MCB.
Page total c/o summary
32 | NSDB-12 (Ground FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.200 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-200 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 300 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 1 No. 25A 4P, MCB (10KA).TYPE-D, 6 Nos. 40A 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b)Spare Space only for 2 Nos.40A 4P, MCB.
Page total c/o summary
33 | ESDB-13 (Ground FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.200 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-200 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 300 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 3 Nos. 25A 4P, MCB (10KA).TYPE-D, 3 Nos. 32A 4P, MCB (10KA).TYPE-D, 4 Nos. 40A 4P, MCB (10KA).TYPE-D, 1 No. 63A 4P, MCCB (25KA).
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b)Spare Space only for 2 Nos.25A 4P, MCB.
Page total c/o summary
34 | NSDB-14 (Ground FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.100 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-100 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 2 Nos. 25A 4P, MCB (10KA).TYPE-D, 3 Nos. 40A 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b)Spare Space only for 2 Nos.40A 4P, MCB.
Page total c/o summary
35 | ESDB-15 (Ground FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.63 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-60 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 4 Nos. 25A 4P, MCB (10KA).TYPE-D, 1 No. 40A 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.25A 4P, MCB
Page total c/o summary
36 | NSDB-16 (Ground FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.100 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-100 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 2 Nos. 25A 4P, MCB (10KA).TYPE-D, 3 Nos. 40A 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.25A 4P, MCB.
Page total c/o summary
37 | ESDB-55 (Ground FL.)for Auditorium Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.250 Amps. 4P MCCB(35 KA Ics) with Adjustable thermal & adjustable magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-250 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 300 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 14 Nos. 25A 4P, MCB (10KA).TYPE-D, 2 Nos. 40A 4P, MCB (10KA).TYPE-D, 1 No. 63A 4P, MCCB (25KA).
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.25A 4P, MCB.
Page total c/o summary
38 | ESDB-56 (Ground FL.)for Auditorium. Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.160 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-160 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 5 Nos. 25A 4P, MCB (10KA).TYPE-D, 4 Nos. 40A 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b)Spare Space only for 2 Nos.25A 4P, MCB.
Page total c/o summary
39 | ESDB-57 (Ground FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.300 Amps. 4P MCCB(35 KA Ics) with Adjustable thermal & Adjustable magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-300 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 400 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 1 No. 63A 4P, MCCB (25KA), 2 Nos. 100A 4P, MCCB (25KA), 1 No. 125A 4P, MCCB (25KA), 1 Nos. 160A 4P, MCCB (25KA).
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.100A 4P, MCCB.
Page total c/o summary
40 | ESDB-17 (1st FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.200 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-200 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 300 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 1 No. 20A 4P, MCB (10KA).TYPE-D, 1 No. 25A 4P, MCB (10KA).TYPE-D, 6 Nos. 32A 4P, MCB (10KA).TYPE-D, 2 Nos. 40A 4P, MCB (10KA).TYPE-D, 1 No. 63A 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.25A 4P, MCB
Page total c/o summary
41 | NSDB-18 (1st FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.160 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-160 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 1 No. 25A 4P, MCB (10KA).TYPE-D, 6 Nos. 40A 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.40A 4P, MCB.
Page total c/o summary
42 | ESDB-19 (1st FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.125 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-120 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 6 Nos. 25A 4P, MCB (10KA).TYPE-D, 3 Nos. 40A 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b)Spare Space only for 2 Nos.25A 4P, MCB
Page total c/o summary
43 | NSDB-20 (1st FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.160 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-160 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 2 Nos. 25A 4P, MCB (10KA).TYPE-D, 4 Nos. 40A 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.40A 4P, MCB.
Page total c/o summary
44 | ESDB-21 (1st FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.250 Amps. 4P MCCB(35 KA Ics) with Adjustable thermal & Adjustable magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-250 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 300 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 7 Nos. 25A 4P, MCB (10KA).TYPE-D, 2 Nos. 40A 4P, MCB (10KA).TYPE-D, 2 Nos. 63A 4P, MCCB (25KA).TYPE-D, 1 No. 100A 4P, MCCB (25KA).
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.25A 4P, MCB.
Page total c/o summary
45 | NSDB-22 (1st FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.160 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-160 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 1 No. 25A 4P, MCB (10KA).TYPE-D, 5 Nos. 40A 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.40A 4P, MCB.
Page total c/o summary
46 | ESDB-23 (1st FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.125 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-120 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 6 Nos. 25A 4P, MCB (10KA).TYPE-D, 2 Nos. 40A 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.25A 4P, MCB.
Page total c/o summary
47 | NSDB-24 (1st FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.125 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-120 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 1 No. 25A 4P, MCB (10KA).TYPE-D, 4 Nos. 40A 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.40A 4P, MCB
Page total c/o summary
48 | ESDB-25 (1st FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.63 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-60 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 5 Nos. 25A 4P, MCB (10KA).TYPE-D, 1 No. 40A 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.25A 4P, MCB.
Page total c/o summary
49 | NSDB-26 (1st FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.63 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-60 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 5 Nos. 25A 4P, MCB (10KA).TYPE-D, 1 No. 40A 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.40A 4P, MCB
Page total c/o summary
50 | ESDB-27 (1st FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.200 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-200 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 300 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 4 Nos. 25A 4P, MCB (10KA).TYPE-D, 2 Nos. 32A 4P, MCB (10KA).TYPE-D, 1 No.40A 4P, MCB (10KA).TYPE-D, 2 Nos. 63A 4P, MCB (10KA).TYPE-D, 1 No. 63A 4P, MCCB (25KA).
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.25A 4P, MCB.
Page total c/o summary
51 | NSDB-28 (1st FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.125 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-120 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 3 Nos. 25A 4P, MCB (10KA), 2 Nos. 40A 4P, MCB (10KA).
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.40A 4P, MCB.
Page total c/o summary
52 | ESDB-29 (2nd. FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.300 Amps. 4P MCCB(35 KA Ics) with Adjustable thermal & Adjustable magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-300 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 400 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 3 Nos. 20A 4P, MCB (10KA).TYPE-D, 2 Nos. 32A 4P, MCB (10KA).TYPE-D, 4 Nos. 40A 4P, MCB (10KA).TYPE-D, 1 No. 63A 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.25A 4P, MCB.
Page total c/o summary
53 | ESDB-30 (2nd. FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.250 Amps. 4P MCCB(35 KA Ics) with Adjustable thermal & Adjustable magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-250 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 300 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 2 Nos. 25A 4P, MCB (10KA), 3 Nos. 32A 4P, MCB (10KA), 2 Nos. 40A 4P, MCB (10KA), 3 Nos. 63A 4P, MCCB (25KA)
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.25A 4P, MCB.
Page total c/o summary
54 | ESDB-31 (2nd. FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.160 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-160 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 1 No. 20A 4P, MCB (10KA).TYPE-D, 5 Nos. 25A 4P, MCB (10KA).TYPE-D, 2 Nos. 32A 4P, MCB (10KA).TYPE-D, 3 Nos. 40A 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.25A 4P, MCB.
Page total c/o summary
55 | ESDB-59 (2nd. FL.) for ICU beds Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.300 Amps. 4P MCCB(35 KA Ics) with Adjustable thermal & Adjustable magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-300 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 400 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 11 Nos. 40A DP, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b)Spare Space only for 2 Nos.25A DP, MCB.
Page total c/o summary
56 | NSDB-32 (2nd. FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.200 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-200 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 300 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 5 Nos. 40A, 4P, MCB (10KA).TYPE-D
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.40A 4P, MCB.
Page total c/o summary
57 | ESDB-33 (2nd. FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.400 Amps. 4P MCCB(35 KA Ics) with Adjustable thermal & Adjustable magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-400 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 500 Amps. TP&N Aluminium bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 6 Nos. 25A, 4P, MCB (10KA).TYPE-D, 1 No. 40A, 4P, MCB (10KA).TYPE-D, 3 Nos. 63A, 4P, MCB (10KA).TYPE-D, 2 Nos. 63A, 4P, MCCB (25KA).
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.25A 4P, MCB.
Page total c/o summary
58 | NSDB-34 (2nd. FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.160 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-160 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 2 Nos. 25A, 4P, MCB (10KA).TYPE-D, 4 Nos. 40A, 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.40A 4P, MCB.
Page total c/o summary
59 | ESDB-35 (2nd. FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.200 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-200 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 300 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 8 Nos. 25A, 4P, MCB (10KA).TYPE-D, 2 Nos. 63A, 4P, MCCB (25KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.25A 4P, MCB.
Page total c/o summary
60 | NSDB-36 (2nd. FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.160 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-160 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 5 Nos. 40A, 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b)Spare Space only for 2 Nos.40A 4P, MCB.
Page total c/o summary
61 | ESDB-37 (2nd. FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.100 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-100 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 1 No. 20A, 4P, MCB (10KA).TYPE-D, 5 Nos. 25A, 4P, MCB (10KA).TYPE-D, 2 Nos. 40A, 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.40A 4P, MCB.
Page total c/o summary
62 | ESDB-38 (2nd. FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.100 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-100 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 4 Nos. 25A, 4P, MCB (10KA).TYPE-D, 1 No. 40A, 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.25A 4P, MCB.
Page total c/o summary
63 | ESDB-58 (2nd. FL.) for OT UPS Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.400 Amps. 4P MCCB(35 KA Ics) with Adjustable thermal & Adjustable magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-400 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 500 Amps. TP&N Aluminium bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 8 Nos. 63A, 4P, MCCB (25 KA Ics).
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.63A 4P, MCCB.
Page total c/o summary
64 | ESDB-39 (3rd. FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.200 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-200 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 300 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 11 Nos. 25A, 4P, MCB (10KA).TYPE-D, 2 Nos. 40A, 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.25A 4P, MCB.
Page total c/o summary
65 | NSDB-40 (3rd. FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.125 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-120 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 4 Nos. 40A, 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.40A 4P, MCB.
Page total c/o summary
66 | ESDB-41 (3rd. FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.100 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-100 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 4 Nos. 25A, 4P, MCB (10KA).TYPE-D, 1 Nos. 40A, 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.25A 4P, MCB.
Page total c/o summary
67 | NSDB-42 (3rd. FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.160 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-160 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 4 Nos. 40A, 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.40A 4P, MCB.
Page total c/o summary
68 | ESDB-43 (3rd. FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.160 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-160 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 6 Nos. 25A, 4P, MCB (10KA).TYPE-D, 3 Nos. 40A, 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.25A 4P, MCB.
Page total c/o summary
69 | NSDB-44 (3rd. FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.200 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-200 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 300 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 1 No. 25A, 4P, MCB (10KA).TYPE-D, 5 Nos. 40A, 4P, MCB (10KA).TYPE-D
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.40A 4P, MCB.
Page total c/o summary
70 | ESDB-45 (3rd. FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.100 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-100 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 1 No. 16A, 4P, MCB (10KA).TYPE-D, 3 Nos. 25A, 4P, MCB (10KA).TYPE-D, 3 Nos. 40A, 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.25A 4P, MCB.
Page total c/o summary
71 | NSDB-46 (3rd. FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.160 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-160 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 4 Nos. 40A, 4P, MCB (10KA).TYPE-D, 1 No. 63A, 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.40A 4P, MCB.
Page total c/o summary
72 | ESDB-47 (4th. FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.200 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-200 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 300 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 4 Nos. 25A, 4P, MCB (10KA).TYPE-D, 2 Nos. 40A, 4P, MCB (10KA).TYPE-D, 2 No. 63A, 4P, MCCB (25KA)..
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.25A 4P, MCB.
Page total c/o summary
73 | NSDB-48 (4th. FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.160 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-160 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 4 Nos. 40A, 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.40A 4P, MCB.
Page total c/o summary
74 | ESDB-49 (4th. FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.160 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-160 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 3 Nos. 25A, 4P, MCB (10KA).TYPE-D, 2 Nos. 40A, 4P, MCB (10KA).TYPE-D, 1 Nos. 63A, 4P, MCCB (25 KA (Ics)).
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.25A 4P, MCB.
Page total c/o summary
75 | NSDB-50 (4th. FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.160 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-160 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 4 Nos. 40A, 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.40A 4P, MCB
Page total c/o summary
76 | NSDB-51 (4th. FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.200 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-200 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 300 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 5 Nos. 25A, 4P, MCB (10KA).TYPE-D, 4 Nos. 40A, 4P, MCB (10KA).TYPE-D, 1 No. 63A, 4P, MCCB (25 KA (Ics)).
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.25A 4P, MCB.
Page total c/o summary
77 | ESDB-52 (4th. FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.200 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-200 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 300 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 6 Nos. 40A, 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.40A 4P, MCB.
Page total c/o summary
78 | ESDB-53 (4th. FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.125 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-120 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 3 Nos. 25A, 4P, MCB (10KA).TYPE-D 4 Nos. 40A, 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.25A 4P, MCB.
Page total c/o summary
79 | NSDB-54 (4th. FL.) Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.160 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-160 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 1 No. 25A, 4P, MCB (10KA).TYPE-D, 4 Nos. 40A, 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.40A 4P, MCB.
Page total c/o summary
80 | ELEVATOR PANEL-1&2 Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 02
INCOMER : 1 No.200 Amps. 4P MCCB(35 KA Ics) with Adjustable thermal & Adjustable magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-200 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 4 Nos. 40 Amps, 4P, MCCB (25 KA (Ics)), 1 Nos. 40A, 4P, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.40A/63A 4P, MCB/MCCB
Page total c/o summary
81 | ELEVATOR PANEL-3 Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.125 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-120 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 2 Nos. 40 Amps, 4P, MCCB (25 KA (Ics)). 1 Nos. 63A, DP, MCB (10KA).TYPE-D
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.63A DP, MCB. (c) Spare Space only for 1 No.63A 4P, MCCB.
Page total c/o summary
82 | ELEVATOR PANEL-4 Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 01
INCOMER : 1 No.100 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-100 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 2 Nos. 40 Amps, 4P, MCCB (25 KA (Ics)), 1 Nos. 63A, DP, MCB (10KA).TYPE-D.
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.63A DP, MCB. (c) Spare Space only for 1 No.63A 4P, MCCB.
Page total c/o summary
83 | ELEVATOR PANEL- 5 & 6 Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 02
INCOMER : 1 No.63 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-100 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 100 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 1 No. 40 Amps, 4P, MCCB (25 KA (Ics)). 1 No. 40A, DP, MCB (10KA).TYPE-D
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.40A DP, MCB. (c) Spare Space only for 1 No.63A 4P, MCCB.
Page total c/o summary
84 | MAIN PANEL FOR KITCHEN Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. | Each | 02
INCOMER : 1 No.160 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-100 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
BUS BARS : 1 Set of 200 Amps. TP&N Copper bus bars of suitable length, Bus bars shall be insulated by heat shrinkable sleaves & clip on shrounds for joints. Bus bars shall be designed to with stand a fault level of 25 KA at 415 volts.
OUTGOINGS : 2 Nos. 25A, 4P, MCB (10KA).TYPE-D, 2 Nos. 40A, 4P, MCB (10KA).TYPE-D, 16 Nos. 16A, DP, RCBO (100mA), 15 Nos. 25A, DP, RCBO (100mA), 2 Nos. 16A, DP, MCB (10KA).TYPE-D, 2 Nos. 25A, DP, MCB (10KA).TYPE-D, 2 Nos. 32A, DP, MCB (10KA)
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection. (b) Spare Space only for 2 Nos.40A DP, MCB. (c) Spare Space only for 1 No.63A 4P, MCCB.
Page total c/o summary
85 | MDB CUM METER BOARD FOR TYPE-IV QTRS Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor/wall mounted totally enclosed , painted after seven tank process, extensible on both sides, switch board suitable for use on 1-Phase/3-phase,50 Hz system having required fault capacity, housed with incoming and outgoing, copper bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required.(Type-IV md accn) | Each | 01
INCOMER : 1 No.40 Amps. 4P MCB(10 KA)
BUS BARS : 100 Amps. TP&N aluminium bus bars
OUT GOINGS : Space for 4 Nos. three phase electronic meters, 4 Nos. 25A 4P, MCB (10KA), 1 Nos. 6A DP MCB (10KA).
Note :- (a) All MCCB's shall have heavy duty solid neutral link & 3 Nos. Spreader Terminals Links for all outgoing MCCB for cable connection.
86 | UPS BYPASS PANEL (for 20,22,24,30 KVA UPS) Supplying, installation, testing and commissioning of UPS bypass panel made of 1.6 mm thick CRCA sheet steel enclosure of approved make design and painted with approved paint shade complete with cotrol wiring, including following :- | Each | 22
INCOMER : 1 No.63 Amps. 4P MCCB(25 KA Ics) with Adjustable thermal & fixed magnetic releases. 1 No.63 Amps. 4P, 415 volts, BYPASS SWITCH complete with handle ,extension shaft, channel set.
INDICATING PANEL (i) Voltmeter of range 0-500 volts with selector switch. (ii) Ammeter of range 0-60 Amps. with selector switch and required CT's. (iii) 3 nos. phase indicating lamps, each lamp shall have one toggle switch backed up with HRC fuse.
Page total c/o summary
87 | Refrifgerator electric driven, single phase, capacity 300/310 litres, frost free, AC, 230 volts all as specified of approved make as directed by GE . | Each | 07
88 | Refrifgerator electric driven, single phase capacity 180 litres, frost free AC, 230 volts all as specified of approved make as directed by GE . | Each | 74
89 | Water cooler, electric driven, single phase, 230 volts AC, having storage capacity 80 Ltr and cooling capacity 40 ltr per hour and connecting to existing water supply line with G.I. pipe of suitable dia complete all as specified of approved make as directed by GE. | Each | 50
90 | Water cooler, electric driven, single phase, 230 volts AC, having storage capacity 180 Ltr and cooling capacity 150 ltr per hour and connecting to existing water supply line with G.I. pipe of suitable dia complete all as specified of approved make as directed by GE. | Each | 05
91 | Water cooler, electric driven, single phase, 230 volts AC, having storage capacity 120 Ltr and cooling capacity 60 ltr per hour and connecting to existing water supply line with G.I. pipe of suitable dia complete all as specified of approved make as directed by GE. | Each | 04
92 | Deep freezer, hard top, 320 ltr capacity, double door, AC 230 volts complete all as specified of approved make as directed by GE. | Each | 09
93 | Voltage stablizers, auto operation, single phase,naturally air cooled, indoor type, designed for input voltage variation 170 to 250 v and out put stablized 230v with accuracy of +/- 2.5%, of capacity 1 KVA, connecting to existing electric point and equipment complete all as specified of approved make as decided by GE. | Each | 77
Page total c/o summary
94 | Voltage stablizers, auto operation, single phase,naturally air cooled, indoor type, designed for input voltage variation 170 to 250 v and out put stablized 230v with accuracy of +/- 2.5%, of capacity 2 KVA, connecting to existing electric point and equipment complete all as specified of approved make as decided by GE. | Each | 07
95 | Voltage stablizers, auto operation, single phase,naturally air cooled, indoor type, designed for input voltage variation 170 to 250 v and out put stablized 230v with accuracy of +/- 2.5%, of capacity 3 KVA, connecting to existing electric point and equipment complete all as specified of approved make as decided by GE. | Each | 68
96 | Voltage stablizers, auto operation, single phase,naturally air cooled, indoor type, designed for input voltage variation 170 to 250 v and out put stablized 230v with accuracy of +/- 2.5%, of capacity 5 KVA, connecting to existing electric point and equipment complete all as specified of approved make as decided by GE. | Each | 07
97 | Split type air conditioner 1.5 Ton capacity, single phase, air cooled complete in all respects | Each | 02
Page total c/o summary

## SECTION-A
Ser No | Description of Work | Drg. No. | Unit | No of Units required | Unit Rate to be quoted by contractor in figures and words in Rs. | Amount
1 | 2 | 3 | 4 | 5
Wiring for OTM & Md ACCN
1 | Point wiring with 1.5 sqmm copper conductor cable (multistrand) PVC insulated FRLS (unsheathed), concealed type,drawing in and including PVC conduit ISI marked having wall thickness not less than 2mm of suitable dia with sunk cast iron/pressed steel terminal boxes made out of 1.2mm thick sheet covered with 3mm thick IS-2036 marked laminated sheet cover (for mounting switches, sockets, regulators etc.), independent, for one light/fan point or for 3 pin 5 Amp socket outlet controlled by one, one way switch including 1.5 sqmm PVC insulated FRLS (unsheathed) copper conductor continuous earth wire complete all as specified. | As applicable as per list of drawings attached for all items | Per Point | 3416
2 | All as per Srl Item 1 above but for one additional light point on the same switch circuit (Two light points controlled by one switch). |  | Per Point | 24
3. | All as per Srl Item 1 above but for two additional light points on the same switch circuit (Three light points controlled by one switch). |  | Per Point | 26
4 | All as per Srl Item 1 above but for three additional light points on the same switch circuit (Four light points controlled by one switch). |  | Per Point | 8
5 | All as per Srl Item 1 above but for one light point controlled by two, 2 way switches. |  | Per Point | 24
6 | All as per Srl item 01 above but for 3 pin socket outlet 15 Amps / 20 Amps with 4 sqmm copper conductor cable and 4 sqmm copper conducter cables as earth wire. |  | Per Point | 517
7 | All as per Srl item 01 above but in stove enamelled steel conduit. |  | Per Point | 62
8 | All as per Srl item 7 above but for one additional light point on the same switch circuit (Two light points controlled by one switch) |  | Per Point | 06
9 | All as per Srl item 7 above but for two additional light points on the same switch circuit (Three light points controlled by one switch) |  | Per Point | 04
10 | All as per Srl item 7 above but for three additional light point on the same switch circuit (Four light points controlled by one switch) |  | Per Point | 01
11 | All as per Srl item 7 above but for one light point controlled by two, 2 way switches. |  | Per Point | 01
12 | All as per Srl item 07 above but for 3 pin socket outlet 15 / 20 Amp with 4 sqmm copper conductor cable and 4 sqmm copper conductor cable as earth wire. |  | Per Point | 05
13 | All as per Srl item 01 above but in stove enamelled steel ERW conduit for flame proof fittings. |  | Per Point | 05
14 | All as per Srl item 13 above but for one addditional light point on the same switch circuit (Two light points controlled by one switch) |  | Per Point | 22
15 | Switch piano, flush button single pole one way, 5 Amp complete all as specified. |  | Each | 3425
16 | Switch piano, flush type, 5 Amp, single pole, two way complete all as specified. |  | Each | 48
17 | Switch piano, flush button, single pole, one way, 15 Amp complete all as specified. |  | Each | 501
18 | Socket outlet 5 pin, 5 Amp, flush type complete all as specified. |  | Each | 453
19. | Socket outlet, 2 in 1, 6 pin, 5 and 15 Amp complete all as specified. |  | Each | 501
20 | Ceiling rose, surface bakelite, 65x50mm, three terminals complete all as specified. |  | Each | 1793
21 | Bell push, flush type, 5 Amp complete all as specified. |  | Each | 99
22 | Sheet metal enclosure with socket plug top and MCB, 240V,SPN industrial socket with two pin and earth metal enclosed plug top along with 20 Amp SP MCB with chained metal cover for the socket outlet complete with connections etc all as specified. |  | Each | 18
23 | Flame proof switch 5 Amp, single pole, one way, complete with encloser. |  | Each | 14
24 | Sub main wiring two single core PVC insulated unsheathed, multistrand, copper conductor flexible, unshethed, FRLS Cable, drawing in and including conduit, concealed type, with all fittings and continuous earth wire of PVC insulated unsheathed FRLS copper conductor cable complete all as specified, of following sizes :-
| (a) 2x6 sq.mm+1x4sq.mm in 25mm dia PVC conduit, ISI marked. |  | RM | 743
| (b) 4x6 sq.mm+2x4sq.mm in 32mm dia PVC conduit, ISI marked. |  | RM | 917
| (c) 4x10 sq.mm+2x6sq.mm in 32mm dia PVC conduit, ISI marked. |  | RM | 20
| (d) 4x6 sq.mm+2x4sq.mm in 32mm dia in stove enamelled steel conduit. |  | RM | 60
Note : Two single core PVC cable, earth wire and PVC conduit shall to be measured as one unit i.e. one RM.
Wiring for Main Hospital Building
25 | Point wiring with 1.5sqmm Copper Conductor Cable (multistrand) PVC insulated FRLS (unsheathed), concealed type, drawing in and incl stove enamelled steel conduit of suitable dia having wall thickness not less than 1.6mm, with 1.6mm thick G.I./metal boxes of suitable size or module numbers for modular switches/sockets and fan regulators incl outer plate and inner adjustable plate (for mounting modular switches, sockets, regulators etc.), independent, for one light/fan point or for 3 pin 5 Amp socket outlet controlled by one, one way switch including 1.5 sqmm PVC insulated FRLS (unsheathed) copper conductor cables as continuous earth wire complete all as specified. |  | Per Point | 9292
26 | All as per Srl item 25 above but for one additional light point on the same switch circuit (Two light points controlled by one switch) |  | Per Point | 741
27 | All as per Srl item 25 above but for two additional light points on the same switch circuit (Three light points controlled by one switch) |  | Per Point | 154
28 | All as per Srl item 25 above but for three additional light points on the same switch circuit (Four light points controlled by one switch) |  | Per Point | 62
29 | All as per Srl item 25 above but for four additional light points on the same switch circuit (five light points controlled by one switch) |  | Per Point | 35
30 | All as per Srl item 25 above but for five additional light points on the same switch circuit (Six light points controlled by one switch) |  | Per Point | 106
31 | All as per Srl item 25 above but for six additional light points on the same switch circuit (Seven light points controlled by one switch) |  | Per Point | 04
32. | All as per Srl item 25 above but for seven additional light points on the same switch circuit (Eight light points controlled by one switch) |  | Per Point | 04
33. | All as per Srl item 25 above but for eight additional light points on the same switch circuit (Nine light points controlled by one switch) |  | Per Point | 02
34. | All as per Srl item 25 above but for nine additional light points on the same switch circuit (Ten light points controlled by one switch) |  | Per Point | 05
35 | All as per Srl item 25 above but for ten additional light points on the same switch circuit (Eleven light points controlled by one switch) |  | Per Point | 02
36 | All as per Srl item 25 above but for one light point controlled by two, 2 way switches. |  | Per Point | 80
37 | All as per Srl item 25 above but for 3 pin socket outlet 15/20 Amp with 4 sqmm copper conductor cable and 4 sqmm copper conductor cable as earth wire. |  | Per Point | 2425
38 | Point wiring for 250 volts, 32 Amp, polycarbonate industrial 3 pin (IP 65/66) socket outlet, independent, with 32 Amps double pole MCB in poly carbonate enclosure , including circuit wiring of any length from the distribution board or/ switch board etc. with two 6 sqmm. PVC insulated, stranded, flexible unsheathed, FRLS copper conductor single core cable, concealed type, drawing in and including stove enamelled steel conduit of suitable dia having wall thickness not less than 1.6mm along with one x 4 sqmm. PVC insulated, stranded, unsheathed, flexible, FRLS copper conductor cable for loop earthing etc. as required complete with 1.6mm thick G.I./metal boxes of suitable size or module numbers |  | Per Point | 28
for modulor switches/ sockets and fan regulators incl outer plate and inner adjustable plate for mounting modulor switches, sockets, regulators etc. complete all as specified.
39 | Point wiring for 415 volts, 32 Amp, polycarbonate industrial 4 pin (IP 65/66) socket outlet, independent, with 32 Amps TPN MCB in poly carbonate enclosure , including circuit wiring of any length from the distribution board or/ switch board etc. with three 6 sqmm. PVC insulated, stranded, unsheathed flexible FRLS copper conductor single core cable, concealed type, drawing in and including stove enamelled steel conduit of suitable dia having wall thickness not less than 1.6mm along with |  | Per Point | 15
one 4 sqmm. PVC insulated, stranded, unsheathed, flexible FRLS copper conductor cable for loop earthing etc. as required complete with 1.6mm thick G.I./metal boxes of suitable size or module numbers for modulor switches/sockets and fan regulators incl outer plate and inner adjustable plate for mounting modulor switches, sockets, regulators etc. complete all as specified.
40 | Stove enamelled black steel conduit having wall thickness not less than 1.6mm, concealed type, inclusive of all fittings such as elbows, tees, bends, reducers etc. as reqd..(Blank conduit for cables), of following external dia :-
| (a) 25mm dia |  | RM | 100
| (b) 32 mm dia |  | RM | 500
| (c) 40 mm dia |  | RM | 550
| (d) 50 mm dia |  | RM | 150
41 | Modular plate type Switch, one way, 6 Amp complete all as specified. |  | Each | 11917
42 | Modular plate type Switch, two way, 6 Amp complete all as specified. |  | Each | 162
43 | Modular plate type Switch, one way, 16 Amp complete all as specified. |  | Each | 2323
44 | Modular plate type Switch, one way, 25 Amp complete all as specified. |  | Each | 10
45 | Modular plate type 6 Amp, 3 pin, socket outlet complete all as specified. |  | Each | 1893
46 | Modular plate type 6/16 Amp, 5 pin, socket outlet complete all as specified. |  | Each | 2323
47 | Modular plate type switch 5 nos one way 6 Amp + 4 nos 16 Amp 1 way switch + 4 nos 3 pin 6 Amp Socket + 4 nos 16 Amp 3 pin socket outlet complete all as specified. |  | Each | 12
48 | Modular plate type switch 4 nos one way 16 Amp + 2 nos 25 Amp 1 way switch + 4 nos 3 pin 16 Amp & 2 nos 3 pin 25 Amp socket outlet complete all as specified |  | Each | 11
49 | Modular plate type switch, one way, 6 Amp, Bell push complete all as specified. |  | Each | 42
50 | Modular plate type, Electronic Fan regulator, 5 steps speed complete all as specified. |  | Each | 1699
51 | Flourscent tube light fitting 1x 36W mounting rail for flourscent light with special integral lamp holder and bracket complete with copper ballast, pf improvement capacitor, starter, tube rod etc. all accessories prewired fixed directly on ceiling/ wall including connections with 1.5 sq. mm. PVC insulated flexible copper wire complete all as specified. Make : Phillips Cat No. TMS 021 / 136 HF-E or equivalent of makes mentioned in Appx 'B' |  | Each | 1131
52 | Flourscent tube light fitting 2x 36W mounting rail for flourscent light with special integral lamp holder and bracket complete with copper ballast, pf improvement capacitor, starter, tube rod etc. all accessories prewired fixed directly on ceiling/ wall including connections with 1.5 sq. mm. PVC insulated flexible copper wire complete all as specified. Make : Phillips Cat No. TMS 021 / 236 HF-E or equivalent of makes mentioned in Appx 'B' |  | Each | 36
53 | Flourscent tube light fitting 1x18 W deccobatten, slim plus and slimlite electronics complete with copper ballast, pf improvement capacitor, starter, tube rod etc. all accessories prewired fixed directly on ceiling/ wall including connections with 1.5 sq. mm. PVC insulated flexible copper wire complete all as specified. Make : Phillips Cat No. TMS 500 /118 or equivalent of makes mentioned in Appx 'B' |  | Each | 282
54 | Flourscent tube light fitting 36/40 W, epoxy finished LM 6 Aluminium housing with inbuilt control gear flame proof complete with copper ballast, pf improvement capacitor, starter, lamp, heat resistance tubular glass & control gear, etc, all accessories prewired fixed directly on ceiling/ wall including connections with 1.5 sq. mm. PVC insulated flexible copper wire complete all as specified. Make : Bajaj Cat part No. BJFFTL-140 or equivalent of makes mentioned in Appx 'B' |  | Each | 27
55 | Ceiling light fitting decorative mounting luminaire with perforated frame and Opal PMMA diffuser 2x11 watt CFL complete with lamp, copper electronic ballast, etc complete all as specified. Make : Philips cat Part No. FBS 300218P5HF or equivalent of makes mentioned in Appx 'B' |  | Each | 12
56 | Down lighter 1x25 W CFL decotwist complete with lamp, copper ballast, etc complete all as specified. Make : Philips Cat part no: FCS 100/118 or equivalent of makes mentioned in Appx 'B'. |  | Each | 264
57 | Surface mounted celing light fitting 1x18W CFL complete with lamp, copper ballast, etc complete all as specified. Make : Philips Cat part no: Deco Twist Lux WW BCS 1902 or equivalent of makes mentioned in Appx 'B' |  | Each | 28
58 | Wall bracket light fitting 1x18W CFL complete with lamp, copper ballast, etc complete all as specified. Make : Philips Cat no: FL 800/320 or equivalent of makes mentioned in Appx 'B' |  | Each | 212
59 | Wall bracket light fitting 1x9/11W CFL complete with lamp, copper ballast, etc complete all as specified. Make : Philips Cat part no: FL 800/320 or equivalent of makes mentioned in Appx 'B' |  | Each | 240
60 | Fluorscent tube light fitting 4x18W mirror optic recess mounting with ballast, holders, starters, tube rods etc. all accessories pre-wired with 1.5 Sqmm copper cable and making connection complete all as specified. Make : Phillips Cat Part No : TBS 369/418MDGNHF or equivalent of makes mentioned in Appx 'B' |  | Each | 2000
61 | Flourscent tube light fitting decorative recessed mirror optic 2x36W CFL indirect luminaire with ballast, holders, starters, all accessories pre-wired including lamp and making connection complete all as specified. Make : Phillips Cat Part No : FBS 580/236 CNN OD MM EBS or equivalent of makes mentioned in Appx 'B' |  | Each | 221
62 | Fluorscent tube light fitting 4x14W T-5 diffused luminaire with ballast, holders, starters, all accessories pre-wired including lamp and making connection complete all as specified. Make : Phillips Cat Part No : TBS 570/414 FNC OD MM HF or equivalent of makes mentioned in Appx 'B'. |  | Each | 413
63 | Clean room luminaire suitable for 3x36 W PL 'L' lamps, all accessories pre-wired including lamp and making connection complete all as specified. Make : Phillips Cat Part No : FCS 650 3x36W PL-L EB BO GT or equivalent of makes mentioned in Appx 'B'. |  | Each | 65
64 | Down lighter fitting 2x13W CFL with ballast, holders, all accessories pre-wired including CFL lamp and making connection complete all as specified. Make : Phillips Cat Part No : FBH 145/213HF or equivalent of makes mentioned in Appx 'B'. |  | Each | 1825
65 | Down lighter fitting 2x18W CFL with ballast, holders, all accessories pre-wired including CFL lamp and making connection complete all as specified. Make : Phillips Cat Part No : FBH 145/218HF (EBW) or equivalent of makes mentioned in Appx 'B'. |  | Each | 373
66 | Down lighter fitting 2x18W CFL with frosted glass, ballast, holders, all accessories pre-wired including CFL lamp and making connection complete all as specified. Make : Phillips Cat Part No : FBH 145/218L or equivalent of makes mentioned in Appx 'B'. |  | Each | 161
67 | Down lighter fitting 1x18W CFL with ballast, holders including CFL lamp and making connection complete all as specified. Make : Phillips Cat Part No : FBH 145/118 HF or equivalent of makes mentioned in Appx 'B'. |  | Each | 80
68 | Flourscent tube light fitting, wallux type, 1x36W wall washer with ballast, holders, starters, all accessories pre-wired including lamp and making connection complete all as specified. Make : Phillips Cat Part No : TMS-520/136 HF or equivalent of makes mentioned in Appx 'B'. |  | Each | 803
69 | Mirror light fitting 1x13W CFL with copper ballast, holders, starters including lamp and making connection with 1.5 Sqmm PVC copper flexible cable complete all as specified. Make : Phillips Cat No : FMC-21/113 or equivalent of Bajaj BSP 118 CFL or equivalent of makes mentioned in Appx 'B' |  | Each | 247
70 | Mirror light fitting 1x36W CFL with copper ballast, holders, starters including lamp and making connection with 1.5 Sqmm PVC copper flexible cable complete all as specified. Make : Phillips Cat No : FMS-600/136 or equivalent of Bajaj BSP 136 CFL or equivalent of makes mentioned in Appx 'B' |  | Each | 113
71 | Flourscent tube light fitting surface type 1x18W with copper ballast, holders, starters, all accessories pre-wired including lamp and making connection with 1.5 Sqmm PVC copper flexible cable complete all as specified. Make : Bajaj Cat No : BCIP 118 LHD or equivalent of makes mentioned in Appx 'B' |  | Each | 153
72 | Light fitting recessed type 1x18W with copper ballast, holders, starters, all accessories pre-wired including lamp and making connection with 1.5 Sqmm PVC copper flexible cable complete all as specified. Make : Bajaj Cat Part No : BSP-118 CFL or equivalent of makes mentioned in Appx 'B'. |  | Each | 33
73 | Flourscent tube light fitting recessed type 1x36W with copper ballast, holders, starters, all accessories pre-wired including lamp and making connection with 1.5 Sqmm PVC copper flexible cable complete all as specified. Make : Phillips Cat Part No : TBS-50/136 HPF or equivalent of makes mentioned in Appx 'B'. |  | Each | 121
74 | Flourscent tube light fitting surface type 1x36W with electronic ballast, holders, starters, all accessories pre-wired including lamp and making connection with 1.5 Sqmm PVC copper flexible cable complete all as specified. Make : Bajaj Cat No : BJSRP 136/140 WEB or Phillips Cat Part No. TCS-605/136 HPF equivalent of makes mentioned in Appx 'B'. |  | Each | 1015
75 | Flourscent tube light fitting surface type 2x36W with electronic ballast, holders, starters, all accessories pre-wired including lamp and making connection with 1.5 Sqmm PVC copper flexible cable complete all as specified. Make :Bajaj Cat Part No : BJP 236/240 W2EB or Phillips Cat Part No. TCS-605/236 HF-E or equivalent makes mentioned in Appx 'B'. |  | Each | 74
76 | Red/Green indiCation light fitting surface type 1x25W holders,including lamp all as specified. (Model as approved by GE). Make : Phillips/ Bajaj/CG/ Hawells. |  | Each | 68
77 | Night light fitting recessed type 1x13W CFL with ballast, holders, starters including lamp complete all as specified. Make : Bajaj Cat Part No. BEOPL-113 CFL or equivalent of makes mentioned in Appx 'B' |  | Each | 221
78 | Patient bed light fitting 1x11W CFL with copper ballast, holders, starters including lamp and making connection with 1.5 Sqmm PVC copper flexible cable complete all as specified. Make : Phillips Cat Part No. FDS-301/111 or equivalent of makes mentioned in Appx 'B'. |  | Each | 774
79 | Ceiling light fitting surface type 2x11W CFL with electronic ballast, holders, including CFL lamp complete all as specified. Make : Phillips Cat Part No : FCS 518/211 PL-S / Bajaj BCSC 218 CFL 2EB or equivalent of makes mentioned in Appx 'B'. |  | Each | 41
80 | Bulkhead fitting 1x9/11 watt CFL complete with lamp, copper ballast, etc complete all as specified. Make : Phillips Cat Part No : FXC 101 or equivalent of makes mentioned in Appx 'B'. |  | Each | 48
81 | Ceiling fan 1050 sweep, AC, 230 Volts, single phase, fixing regulator and making connections from ceiling rose or connector up to fan with 3 core flexible copper cable 23/0076 of suitable length, including numbering etc complete. |  | Each | 43
82 | As per Srl item 81 above but of 1200 sweep. |  | Each | 2070
83 | As per Srl item 81 above but of 1400 sweep. Note for Srl item 81 to 83 : Regulator shall be measured and paid for separately |  | Each | 226
84 | Supply only electronic five speed step fan regulator. |  | Each | 640
85 | GI, medium grade 15mm dia fan down rod as per required length not more than 1.5m long in lieu of existing down rod including threading and making holes and fixing complete. |  | Each | 1699
86 | Exhaust fan of 1400 rpm 300 mm sweep complete with louvers and shutters, fixed on walls by and providing bolts and nuts of suitable size grouted in PCC 1:2:4 blocks of size 150x150x150 mm, mosquito mesh on the inside in the existing opening and making connections with 3 core 1.5 sq mm. copper conductor PVC insulated and PVC sheathed flexible wire complete all as specified. |  | Each | 462
87 | Exhaust fan of 1400 rpm 450 mm sweep complete with louvers and shutters, fixed on walls by and providing bolts and nuts of suitable size grouted in PCC 1:2:4 blocks of size 150x150x150 mm, mosquito mesh on the inside in the existing opening and making connections with 3 core 1.5 sq mm. copper conductor PVC insulated and PVC sheathed flexible wire complete all as specified. |  | Each | 98
88 | Wall bracket fan 400 mm sweep with step speed regualtor (built in) and making connections with 3 core 1.5 sq mm. copper conductor PVC insulated and PVC sheathed flexible wire complete all as specified. |  | Each | 18
89 | Ceiling light fitting complete with lamp, copper ballast, etc complete all as specified. Make : Philips Cat part no: Deco Twist Lux WW BCS 1902 or equivalent of makes mentioned in Appx 'B'. |  | Each | 28
90 | Bell, AC, 230V, single pole, complete all as specified |  | Each | 99
91 | Sheet metal enclosures for DBs when MCBs to be used, double door including making connections etc. IP 42 protection, of following sizes :-
| (a) SPN DB 4 ways with 200 Amp rated bus-bars, 240 volt |  | Each | 04
| (b) SPN DB 8 ways with 200 Amp rated bus-bars, 240 volt |  | Each | 83
| (c) SPN DB 12 ways with 200 Amp rated bus-bars, 240 volt |  | Each | 03
| (d) TPN DB 4 ways with 200 Amp rated bus-bars, 415 volts |  | Each | 46
| (e) TPN DB 8 ways with 200 Amp rated bus-bars, 415 volts |  | Each | 126
| (f) TPN DB 12 ways with 200 Amp rated bus-bars, 415 volts |  | Each | 09
| (g) TPN DB 8 ways with 200 Amp rated bus-bars Vertical DB, 415 volts |  | Each | 11
| (h) TPN DB 12 ways with 200 Amp rated bus-bars Vertical DB, 415 volts |  | Each | 03
| (j) TPN DB 6 ways with 200 Amp rated bus-bars, 415 volts |  | Each | 190
| (k) SPN DB 2 ways without busbar, 240 volts |  | Each | 03
92 | MCCB, 4 pole, 80 Amps, rapturing capacity 25 KA (Ics), 415 volts micro processor type complete all as specified. |  | Each | 01
93 | ISOLATOR, MCB's complete all as specified, of following capacity :-
| (a) DP ISOLATOR, 240 volts, DP, upto 40 Amps |  | Each | 12
| (b) ISOLATOR, 240 volts, 4 pole, upto 40 Amps |  | Each | 345
| (c) 63 Amps 4P ISOLATOR, 240 volts |  | Each | 32
| (d) 25 Amps SPN RCBO 100mA, 240 volts |  | Each | 453
| (d) 40 Amps SPN RCCB 100mA, 240 volts |  | Each | 461
| (e) 63 Amps SPN RCCB 100mA, 240 volts |  | Each | 66
| (f) 25 Amps 4P RCBO 100mA, 240 volts |  | Each | 04
| (g) 40 Amps 4P RCBO 100mA, 240 volts |  | Each | 03
| (h) 25 Amps DP RCBO 100mA, 240 volts |  | Each | 08
| (j) 25 Amps DP RCCB(ELCB) 100mA, 240 volts |  | Each | 67
| (k) 40 Amps DP RCCB(ELCB) 100mA, 240 volts |  | Each | 71
| (l) SPN MCB, 240 volts, 5 to 30 Amps |  | Each | 35
| (m) SP MCB 5 to 30 Amps, 240 volts |  | Each | 4224
| (n) BLANKING PLATE |  | Each | 1787
94 | Pedestal fan, 600mm sweep with step speed regulator (built in), AC, 230 volts, 50HZ, Single Phase with stainless steel stand and base, 3 core 1.5 Sqmm flexible copper wire of suitable length and top plug complete all as specified (Portable type pedestal fans) |  | Each | 131
95 | Emergency lights with one flourescent tube rod 18/20 W, non metallic type with inbuilt dry battery of suitable capacity atleast for three hours duration, auto switch on during electric power failure and auto switch off during electric power supply on, fixed on walls/ceillings with suitable size copper cable all as specified. |  | Each | 123
96 | Polycarbonate industrial single phase 3 pin socket outlet 250 volts, 32 Amps, SPN in polycarbonate enclosure with 32 Amps SPN MCB complete all as specified. |  | Each | 28
97 | Polycarbonate industrial 3 phase 4 pin socket outlet 415 volts, 32 Amps, TPN in polycarbonate enclosure with 32 Amps SPN MCB complete all as specified. |  | Each | 15
98 | G.I pipe, medium grade, 80 mm dia. with all fittings, laid in plinth protection for incoming power cable as reqd including earth work in any type of soil. |  | RM | 350
99 | Three phase electronic type energy meter 10 - 40 Amp temper proof with LCD display accuracy class 1 complete all as specified. |  | Each | 14
100 | Single phase electronic type energy meter 5 - 20 Amp temper proof with LCD display accuracy class 1 complete all as specified. |  | Each | 84
101 | 63 Amps 4 pole, MCCB with operating handle microprocessor type (25 KA (Ics)) breaking capacity housed in and incl 1.6 mm thick CRCA sheet steel enclosure of approved make and painted in approved shade complete. |  | Each | 03
102 | 100 Amps 4 pole, MCCB with operating handle microprocessor type (25 KA (Ics)) breaking capacity housed in and incl 1.6 mm thick CRCA sheet steel enclosure of approved make and painted in approved shade complete. |  | Each | 02
103 | 125 Amps 4 pole, MCCB with operating handle microprocessor type (25 KA (Ics)) breaking capacity housed in and incl 1.6 mm thick CRCA sheet steel enclosure of approved make and painted in approved shade complete. |  | Each | 01
104 | 160 Amps 4 pole, MCCB with operating handle microprocessor type (25 KA (Ics)) breaking capacity housed in and incl 1.6 mm thick CRCA sheet steel enclosure of approved make and painted in approved shade complete. |  | Each | 01
105 | 200 Amps 4 pole, MCCB with operating handle microprocessor type (25 KA (Ics)) breaking capacity housed in and incl 1.6 mm thick CRCA sheet steel enclosure of approved make and painted in approved shade complete. |  | Each | 01
106 | 25 Amps 4 pole, MCB (10 KA) 415 volts complete. |  | Each | 06
107 | 35 to 60 Amps 4 pole, MCB (10KA) 415 volts complete. |  | Each | 07
108 | Earthing complete with copper earth plate electrode of size 600x600x3.15mm thick, buried directly in ground (earth pit not less than 2.25 meters deep below ground level) with top edge not less then 1.5 meter below normal ground level, connected with copper earthing lead of 20x3mm strip by means of bolts and nuts, check nuts and washer of galvanized iron or steel, 40mm dia G.I. med grade protection pipe up to 7.5m length, G.I. med grade watering pipe 20mm dia with funnel, wire mesh, coal, salt etc, PCC 1:2:4 type B-1 in earth pit covered with C.I. cover complete all as shown in plate No. 3 of SSR Part-I connected to earthing test point all as specified or indicated including testing on completion. |  | Each Set | 80
109 | Copper strip for bus earthing of size 100x10mm incl supporting/holding clamps of G.I. strip of suitable size grouted in PCC 1:2:4 type B-1 blocks of size 150x150x300mm saddles incl screws, nuts/bolts etc for incoming and outgoing earthing lead connections complete all as specified. |  | RM | 100
110 | Earth lead connection with 20x3mm copper strip from earth electrode or on cable tray etc as reqd, fixed on walls, laid in floors or passed through pipes complete all as specified. |  | RM | 8910
111 | 15 mm dia medium grade GI pipe as protection pipe, laid in trenches or fixed on walls or poles all as specified. |  | RM | 0
Telephone & TV Wiring (For OTM & Married Accn. Only)
112 | PVC conduit, concealed type, 25mm dia having wall thickness not less than 2mm, ISI marked inclusive of all fittings such as elbows, tees, bends, reducers etc. as reqd fixed in chases/under floors/slab etc. complete all as specified. |  | RM | 4341
113 | Metal box on surface/ in recess with 3mm phenolic cover for mounting switch socket etc as reqd, of following size :-
| (a) 75x75 mm box. |  | Each | 180
| (b) 175x100 mm box |  | Each | 44
114 | Telephone M.S. tag box with hinged cover having locking arrangement as per telephone deptt approval and having 10 pair tag etc. as reqd. |  | Each | 27
115 | Supplying and fixing the following in the existing sheet steel box including connections etc. as reqd.
| (a) RJ 11 Telephone socket |  | Each | 113
| (b) TV socket |  | Each | 113
116 | 2 pair, 0.51 mm PVC insulated, PVC sheathed annealed tinned copper conductor telephone wire drawing in existing conduit all as specified. |  | RM | 2100
117 | Gal Iron 50 mm dia, med grade pipe laid in plinth protection for incoming TV/Tel. cable as protection pipe incl earth work in any type of soil complete. |  | RM | 205