## Part- (AIRCONDITIONING)
Ser No. | Description of Work | Unit | No of Units required | Unit Rate to be quoted by contractor in figures and words in Rs. | Amount
1 | 2 | 4 | 5 | 6 | 7
Water Chilling Unit
1. | Supplying, fixing, testing and commissioning hermatically sealed water cooled centrifugal chilling unit 750 TR capacity complete with open/semi/hermatically sealed compressor with motor condenser, chiller, controls, microprocessor based control panel, VFD panel with ACB, digital voltmeter & ammeter for incoming supply & load interconnecting refrigerant piping, base frame, concerete base for mounting the unit complete all as per specified with following features. Chilled water in : 12.2O C Chilled water out : 6.6O C Chiller F.F. : 0.0005 750 TR (Actual) | Each | 3 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
Pump Set
2. | Supplying, fixing, testing and commissioning horizontal split casing type water circulating pump sets complete with motor, base plate foundation etc. complete all as specified with following features/fixtures :-
| (a) Chilled water pump, horizontal split casing type, 1800 USGPM at 40m. head (one standby). | Each | 3 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (b) Condenser water pumps, horizontal split casing type, 2850 USGPM at 27m. head (one standby). | Each | 3 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| Page total c/o Summary |  |  |  | Rs
Secondary Chilled Water Pumps & Variable Speed Pumping System
3. | Supplying, fixing, testing and commissioning of secondary variable speed pumping system consisting of 2 Nos. secondary pumps, 1 No. dedicated microprocessor based pump controller with parallel pumping software duly downloaded, 2 Nos. adjustable frequency drives and multiple differential pressure sensor/ transmitters as necessary complete all as specified. | Each | 2 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
Secondary chilled water pumps 3600USGPM at 30m. head. (one standby) Note: The entire system alongwith secondary pumps must be sourced from single manufacturer only for unit responsibility. The system shall be complete in all respects and suitable for rating described hereinafter and as per specification.
Cooling Tower
4. | Supplying, fixing, testing and commissioning FRP induced draft type cooling tower complete with FRP basin, FRP body, fan, distribution pipes, overflow pipe, ladder including foundation etc. complete all as specified suitable for 750 TR. | Each | 03 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
Airhandling Unit
5. | Supplying, fixing, testing and commissioning of horizontal double skin floor mounted type airhandling units complete with fan, fan motor, drive, cooling coil, prefilters, microvee filter & HEPA filters, heaters, humidifier, mixing box, strip heaters, HRW canvass connection, fresh air damper with louvers & bird screen, including foundation, vibration isolator pads complete all as specified, of :-
| (a) 20,000 cfm, 8 row coil | Each | 1 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| Page total c/o Summary |  |  |  | Rs
| (b) 6,500 cfm, 8 row coil | Each | 1 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (c) 6,000 cfm, 8 row coil | Each | 1 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (d) 4,500 cfm, 8 row coil | Each | 2 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (e) 4,000 cfm, 8 row coil | Each | 1 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (f) 3,500 cfm, 8 row coil | Each | 2 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (g) 2,500 cfm, 8 row coil | Each | 1 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
Airhandling Unit
6. | Supplying, fixing, testing and commissioning of horizontal double skin floor mounted type airhandling unit complete with fan, fan motor, drive cooling coil prefilters, microvee filter fresh air damper with louvers & bird screen, including foundation, vibration isolator pads complete all as specified, of :-
| (a) 20,000 cfm, 6 row coil | Each | 5 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| Page total c/o Summary |  |  |  | Rs
| (b) 18,000 cfm, 6 row coil | Each | 4 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (c) 16,000 cfm, 6 row coil | Each | 1 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (d) 15,000 cfm, 6 row coil | Each | 3 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (e) 13,000 cfm, 6 row coil | Each | 2 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (f) 10,000 cfm, 6 row coil | Each | 12 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (g) 9,000 cfm, 6 row coil | Each | 9 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (h) 8,000 cfm, 6 row coil | Each | 4 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
Unitary Airhandling Units
7. | Supplying, fixing, testing and commissioning of double skin ceiling mounted unitary type airhandling unit complete with fan, fan motor drive, cooling coil, filters, canvass connections, 2 way throttling valve with snap acting thermostat etc. complete all as specified, of :-
| Page total c/o Summary |  |  |  | Rs
| (a) 6,000 cfm, 6 row coil cooling | Each | 3 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (b) 5,000 cfm, 6 row coil cooling | Each | 2 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (c) 4,000 cfm, 4 row coil cooling | Each | 3 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (d) 3,000 cfm, 4 row coil cooling | Each | 4 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (e) 2,000 cfm, 4 row coil cooling | Each | 2 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
Fan Coil Unit
8. | Supplying, fixing, testing and commissioning of horizontal hide away type fan coil units complete with fan, fan motor, cooling coil, filters, 2 way modulating valve with snap acting thermostat, ball valve with & without strainer at inlet & outlet, including control panel with cabling and earthing complete all as specified, of :- 1.5 Tons (600 cfm) | Each | 2 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| Page total c/o Summary |  |  |  | Rs
Air Purifier
9. | Supplying, fixing, testing and commissioning of Photo hydro ionization cell based on advanced oxidation technology with broad spectrum UV tube duly enclosed in hydrated catalytic matrix cell with the capability to produce friendly oxidizers like hydro peroxides, super oxide ions, ozonide ions & hydroxide ions, duly encased in poly tube to prevent glass or mercury leakage into the atmosphere, the cell will have built in fiber optic device as remote indication of this operation complete all as specified, of :-
| (a) 20,000 cfm | Each | 1 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (b) 6,500 cfm | Each | 1 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (c) 6,000 cfm | Each | 1 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (d) 4,500 cfm | Each | 2 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (e) 4,000 cfm | Each | 1 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (f) 3,500 cfm | Each | 2 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| Page total c/o Summary |  |  |  | Rs
| (g) 2,500 cfm | Each | 1 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
Packaged Type Airwasher
10. | Supplying, fixing, testing and commissioning packaged type airwashers of G.I. construction fabricated from 16 gauge G.I. sheet body, blower housing, centrifugal forward curved blower with motor, drive set, acetate paper cooling pad of 90% effeciency with stainless steel sump and body, pump, water connection, Aluminum filters, canvas connection, mounting base of angle iron/chennel etc. blower & motor mounted on common rail using cushy foot mounting and M.S. frame for supports etc. complete all as specified, of :-
| (a) 40,000 cfm, 50 mm static pressure | Each | 1 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (b) 30,000 cfm, 50 mm static pressure | Each | 1 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
Axial Flow Fan
11. | Supplying, fixing, testing and commissioning axial flow type exhaust fan complete with fan and motor, drive set, mounting frame, mounting accessories canvass connection, gravity damper of G.I. at fan outlet and electric control panel with cabling and earthing complete all as specified (Fan to be suspended from ceiling/ installed on wall with M.S. supports of and mounting accessories etc. and Fan should be interlocked with fire panel of 3,000 cfm, 20 mmwg S.P. each | Each | 14 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
Propeller Type Fan
12. | Supplying, fixing, testing and commissioning of propeller type fan for fresh air supply and exhaust complete all as specified of 5000 cfm, 610 mm dia each | Each | 5 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| Page total c/o Summary |  |  |  | Rs
Exhaust Scrubber
13. | Supplying, fixing, testing and commissioning of centrifugal exhaust scrubber of 18 gauge sheet steel duly powder coated inner & outer construction with fan and motor and drive (both fan and motor shall be mounted on a common frame using cushy foot mounting) with side suction and front discharge including vibration isolator, water tank with float valve, pump, distributor, nozzels, eleminator, piping & valve from tank to pump to distributor, and M.S. frame for supports etc. complete all as specified for 50,000 cfm, 65 mmwg static pressure | Each | 1 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
Air Curtain
14. | Supplying, fixing, testing and commissioning of air curtains with decorative casing, fan, motor, remote etc. complete all as specified of 1500 mm length each | Each | 17 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
Inline Fans
15. | Supplying and fixing inline fans of G.I. construction complete with centrifugal fan with motor, canvass connection at inlet and outlet complete with electric panel with MCB and relays, cabling and earthing complete all as specified, of :-
| (a) 1600 cfm, 20 mm S.P. | Each | 2 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (b) 1000 cfm, 20 mm S.P. | Each | 6 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (c) 800 cfm, 20 mm S.P. | Each | 4 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| Page total c/o Summary |  |  |  | Rs
Hot Water Boiler
16. | Supplying, fixing, testing and commissioning of Horizontal fire tube boiler operative. All accessories, including automatic burner pre heaters interconnecting H.P. flexible/ copper piping. Fuel pumping and blower with damper & auto electric sequence control/ operational panel complete all as specified of 10,00,000 Kcal / Hr (1176 Kw) Each | Each | 3 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
Heat Exchanger
17. | Supplying, fixing, testing and commissioning of plate type heat exchanger of 10,00,000 kcal capacity with stainless steel plates of variable surface with nitril rubber gasket, carbon steel frame, etc. complete in all respect and all as specified. | Each | 3 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
Condenser Water Piping
18. | Supplying, fixing, testing and commissioning `C' class mild steel - black steel pipes in condensor water piping system with all necessary fittings incl bends, tees, reducers, flanges, supports etc. complete all as specified, for
| (a) 600 mm dia | RM | 100 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (b) 300 mm dia | RM | 100 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
19 | Butterfly Valves class 1, PN-1.6 conforming to IS-13095 of 1991 complete with flanges, bolts, nuts, gasket etc. as per specifications, hydroulically tested to 20 kg/cm2 complete in all respects, suitable, for
| (a) 600 mm dia pipe | Each | 3 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| Page total c/o Summary |  |  |  | Rs
| (b) 300 mm dia pipe | Each | 18 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
20 | Cast iron balancing valves conforming to IS, class 1 incl nuts, bolts, gasket etc complete suitable for 300 mm dia pipe. | Each | 3 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
21 | Cast iron double flanged horrizontal type with gun metal seat non-return valve conforming to class 1 of IS-5312 incl nuts, bolts, gasket etc complete for 300mm dia pipe. | Each | 3 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
22 | Pot Strainers incl rubber insertion, bolts, nuts, G.I. flanges etc complete, suitable for following bore of pipes :-
| (a) 600 mm dia | Each | 1 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (b) 300 mm dia | Each | 3 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
23 | Water flow switch (incl for chilled water supply). | Each | 4 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
24 | Pressure gauge (incl for chilled water supply). | Each | 30 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| Page total c/o Summary |  |  |  | Rs
25 | Thermometer (incl for chilled water supply). | Each | 30 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
26 | Flexible Pipe Connection of suitable length for 300 mm bore pipe complete. | Each | 18 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
Chilled Water Piping
27 | Supplying, fixing, testing and commissioning `C' class mild steel black steel pipes with all necessary fittings, supports & insulation etc. complete all as specified, of
| (a) 350 mm dia | RM | 2500 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (b) 250 mm dia | RM | 150 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (c) 200 mm dia | RM | 110 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (d) 125 mm dia | RM | 90 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| Page total c/o Summary |  |  |  | Rs
| (e) 150 mm dia | RM | 250 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (f) 100 mm dia | RM | 300 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (g) 65 mm dia | RM | 250 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (h) 80 mm dia | RM | 350 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (j) 50 mm dia | RM | 1050 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (k) 40 mm dia | RM | 350 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (l) 32 mm dia | RM | 100 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (m) 25 mm dia | RM | 50 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| Page total c/o Summary |  |  |  | Rs
28 | Butterfly Valves class 1, PN-1.6 conforming to IS-13095 of 1991 complete with flanges, bolts, nuts, gasket etc. as per specifications, hydroulically tested to 20 kg/cm2 complete in all respects, suitable for
| (a) 350 mm dia pipe | Each | 6 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (b) 250 mm dia pipe | Each | 18 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (c) 200 mm dia pipe | Each | 6 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (d) 150 mm dia pipe | Each | 4 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (e) 65 mm dia pipe | Each | 18 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (f) 50 mm dia pipe | Each | 64 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
29 | Ball Valves suitable for pipes of dia
| (a) 40 mm with strainer | Each | 10 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| Page total c/o Summary |  |  |  | Rs
| (b) 40 mm without strainer | Each | 10 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (c) 32 mm with strainer | Each | 6 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (d) 32 mm without strainer | Each | 6 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (e) 25 mm with strainer | Each | 2 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (f) 25 mm without strainer | Each | 2 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
30 | Cast iron balancing valves conforming to IS, class 1 incl nuts, bolts, gasket etc complete, suitable for following dia pipes :-
| (a) 350 mm | Each | 1 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (b) 250 mm | Each | 6 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| Page total c/o Summary |  |  |  | Rs
| (c) 200 mm | Each | 3 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (d) 150 mm | Each | 2 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (e) 65 mm | Each | 9 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (f) 50 mm | Each | 32 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
31 | Cast iron double flanged horrizontal type with gun metal seat non-return valve conforming to class 1 of IS-5312 incl nuts, bolts, gasket etc complete, suitable for following dia pipes :-
| (a) 350 mm | Each | 2 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (b) 400 mm | Each | 2 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (c) 250 mm | Each | 3 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| Page total c/o Summary |  |  |  | Rs
32 | Pot Strainer, of size |  |  |  | Rs…………………..…
| (a) 350 mm | Each | 2 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (b) 250 mm | Each | 3 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
33 | Air purge valve (15 mm) | Each | 80 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
34 | Flexible Pipe for Connection of suitable dia and required length of following bores :-
| (a) 350 mm | Each | 4 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (b) 250 mm | Each | 18 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
Expansion Tank
35 | Supplying, fixing, testing and commissioning expansion tank fabricated from 3 mm thick M.S. sheet having 50 mm thick polyurethen foam insulation covered with 26 gauge Aluminium sheet with main hole cover drain, over flow, quick fill, normal water supply connections complete in all respect and all as specified of 4000 litres capacity. | Each | 1 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| Page total c/o Summary |  |  |  | Rs
Drain Piping
36 | Supplying, fixing, testing and commissioning G.I. drain piping complete with fittings, supports valves and 15 mm thick polyurethen foam insulation complete all as specified, for following dia :-
| (a) 50 mm | RM | 110 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (b) 40 mm | RM | 100 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (c) 32 mm | RM | 200 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (d) 25 mm | RM | 200 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
Ducting
37 | Supplying, fixing, testing and commissioning steel metal ducting complete with supports, dampers, etc. all as specified.
(i) G.I. Sheet Metal Ducting (Rectangular), fabricated with
| (a) 0.63 mm (24 Gauge) | Sqm | 8000 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (b) 0.80 mm (22 Gauge) | Sqm | 4125 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| Page total c/o Summary |  |  |  | Rs
| (c) 1.00 mm (20 Gauge) | Sqm | 1100 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (d) 1.25 mm (18 Gauge) | Sqm | 270 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
(ii) Aluminium Ducting (Rectangular), fabricated with
| (a) 0.80 mm (22 Gauge) | Sqm | 5000 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (b) 1.00 mm (20 Gauge) | Sqm | 1500 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
Insulation
38 | Supplying and fixing of glass wool insulation on ducts complete all as specified of 25 mm thickness. | Sqm | 18000 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
39 | Supplying and fixing of UV/fire/water, thermal protective, canvas coating on duct insulation by wrapping canvas cloth dipped in star bond 30-36, complete all as specified. | Sqm | 18000 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
Duct Acoustic Lining
40 | Supplying and fixing of duct acoustic lining with bonded glass insulation of density 32 kg/m3 covered with 26 gauge perforated aluminium sheet with nuts and bolts complete all as specified of 25 mm thickness. | Sqm | 2000 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
Grill
41 | Supplying, fixing, testing and commissioning Aluminium powder coated supply and return air grill/diffusers complete all as specified, for
| Page total c/o Summary |  |  |  | Rs
| (a) Aluminium supply air diffuser with damper. | Sqm | 104 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (b) Aluminium return air diffuser without damper. | Sqm | 104 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (c) Aluminium return air grilles without damper. | Sqm | 6 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
42 | Fresh/Return Air Grill
| (a) Fresh/Exhaust air damper with louvers, bird screen and damper. | Sqm | 22 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (b) Double louvered fresh air grill with damper (for airwasher). | Sqm | 8 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
Fire Damper
43 | Supplying and fixing galvanised sheet fire dampers complete with damper electric actuator, smoke/heat detector, interlocking arrangement with blower motor complete all as specified. (Opening of fire damper in wall/ partition to be cut and later made good to a fire rating of similar capacity as of damper without any extra cost to Govt), for
| (a) Fire dampers | Sqm | 45 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (b) Actuator assembly | Set | 200 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| Page total c/o Summary |  |  |  | Rs
44 | Volume Control Damper Supplying and fixing G.I. volume control damper with blades, adjustable lever, frame etc. complete all as specified. | Sqm | 150 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
45 | Electrical Panel Board (Airconditioning) Supplying, installing, testing and commissioning of factory made LT panel board suitable for 415 volts, 3 phase 4 wire, 50 Hz AC supply fabricated out of CRCA sheet 2.0 mm thick powder coated interrally and externally painted, compartmentalized design fitted with ACB's & MCCB's on common bus bar in tier formation, indoor type, providing and comprising of the following all as specified :- | Each | 01 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
(A) Incoming : 02 Nos 200 Amps capacity triple pole metal clad incoming feeder control panel extensible pattern each provided with under mentioned equipments :-
(i) Electrolytic aluminium bus bar 2000 Amps for phases and 1250 Amps for neutral - 01 Set. (ii) ACB 1600 Amps trip free withdrawable type manual operated with mechanical ON/OFF indicator, auxiliary switches and safety features - 01 No. (iii) CT's of ratio 1600/05 Amps of suitable VA burden and accuracy for protection and metering - 01 Set. (iv) Static trip devices for over current and earth fault - 01 Set.
(v) Under voltage release - 01 No.
(vi) Red and Green indicating lamps to indicate ON/OFF position - 01 Set.
(vii) Flush pattern voltmeter 0-500 volts, square dial with selector switch to measure voltage between phases and between phase and neutral - 01 No.
(viii) Flush pattern Amp meter 0-2000 Amps, square dial with selector switch to measure current in any phase - 01 No.
(ix) Cable boxes/side frame - 01 Set.
| Page total c/o Summary |  |  |  | Rs
(B) Bus Coupler : 01 No. 2000 Amp capacity triple pole metal clad bus coupler panel extensible panel provided with under mentioned equipments :-
(i) Electrolytic aluminium bus bar 2000 Amps for phases and 1250 Amps for neutral - 01 Set.
(ii) ACB 1600 Amps trip free withdrawable type manual operated with mechanical ON/OFF indicator, auxiliary switches and safety features - 01 No. (iii) Red and Green indicating lamps to indicate ON/OFF position - 01 Set. (iv) Electrical/Mechanical inter lock - 01 Set. (v) Cable boxes/side frame - 01 Set.
(C) Out Going
1(a) 02 Nos 1250 Amps capacity triple pole metal clad outgoing feeder control panel extensible pattern each provided with following equipments/accessories :-
(i) Electrolytic aluminium bus bar 2000 Amps for phases and 1250 Amps for neutral - 01 Set. (ii) ACB 1250 Amps trip free withdrawable type manual operated with mechanical ON/OFF indicator, auxiliary switches and safety features - 01 No. (iii) CT's of ratio 1250/05 Amps of suitable VA burden and accuracy for protection and metering - 01 Sets. (iv) Static trip devices for over current and earth fault - 01 Set. (v) Under voltage release - 01 No. (vi) Red and Green indicating lamps to indicate ON/OFF position - 01 Set. (vii) Flush pattern Amp meter 0-1250 Amps, square dial with selector switch to measure current in any phase - 01 No. (viii) Cable boxes/side frame - 01 Set.
1(b) Triple pole metal clad outgoing feeder control panel extensible pattern each provided with following equipments/accessories:-
(i) MCCB TPN 200 Amps with rupturing capacity 35 KA (Ics) complete with thermal magnetic release - 01 Nos.
(ii) CT's of ratio 200/5 Amps of suitable VA burden and accuracy - 01 Set each.
(iii) Red and Green indicating lamps to indicate ON/OFF position - 01 Set each. (iv) Flush pattern Amp meter 0-400 Amps, square dial with selector switch to measure current in phase - 01 No each. (v) Side frame - 01 Set each.
1(c) Triple pole metal clad outgoing feeder control panel extensible pattern each provided with following equipments/accessories :-
(i) MCCB TPN 100 amps with rupturing capacity 35 KA (Ics) complete with thermal magnetic release - 01 No. (ii) CT's of ratio 100/5 Amps of suitable VA burden and accuracy - 01 Set. (iii) Red and Green indicating lamps to indicate ON/OFF position - 01 Set. (iv) Flush pattern Amp meter 0-200 Amps, square dial with selector switch to measure current in phase - 01 No. (v) Side frame - 01 Set.
2(a) 02 Nos 1250 Amps capacity triple pole metal clad outgoing feeder control panel extensible pattern each provided with followings equipments/accessories:-
(i) Electrolytic aluminium bus bar 2000 Amps for phases and 1250 Amps for neutral - 01 Set. (ii) ACB 1250 Amps trip free withdrawable type manual operated with mechanical ON/OFF indicator, auxiliary switches and safety features - 01 No. (iii) CT's of ratio 1250/05 Amps of suitable VA burden and accuracy for protection and metering - 01 Set. (iv) Static trip devices for over current and earth fault - 01 Set. (v) Under voltage release - 01 No. (vi) Red and Green indicating lamps to indicate ON/OFF position - 01 Set. (vii) Flush pattern Amp meter 0-1250 Amps, square dial with selector switch to measure current in any phase - 01 No. (viii) Cable boxes/side frame - 01 Set.
2(b) Triple pole metal clad outgoing feeder control panel extensible pattern each provided with following equipments/accessories:-
(i) MCCB TPN 250 Amps with rupturing capacity 25 KA (Ics) complete with thermal magnetic release - 01 No.
(ii) CT's of ratio 250/5 Amps of suitable VA burden and accuracy - 01 Set each. (iii) Red and Green indicating lamps to indicate ON/OFF position - 01 Set each. (iv) Flush pattern Amp meter 0-300 Amps, square dial with selector switch to measure current in phase - 01 No each. (v) Side frame - 01 Set each.
2(c) Triple pole metal clad outgoing feeder control panel extensible pattern each provided with following equipments/accessories:-
(i) MCCB TPN 100 amps with rupturing capacity 25 KA (Ics) complete with thermal magnetic release - 01 No. (ii) CT's of ratio 100/5 Amps of suitable VA burden and accuracy - 01 Set. (iii) Red and Green indicating lamps to indicate ON/OFF position - 01 Set. (iv) Flush pattern Amp meter 0-200 Amps, square dial with selector switch to measure current in phase - 01 No. (v) Side frame - 01 Set.
2(d) Change over switch on load type TPN 415 volts, 1600 Amps - 01 No.
46 | Supplying, installing, testing and commissioning of main panel board cubical compartmentalised, floor mounted made of 2.0 mm thick steel sheet duly painted complete with voltmeter, ammeter, indicating lights for selector switch, incoming / outgoing feeders CTS contactors for remote control operation, complete all as specified fitted with following accessories. (For Pump etc.) | Each | 1 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
(i) 1 No. 1600 Amps ACB incoming.
(ii) 1 set 1600 Amps ACB TPN and neutral copper conductor bus bars duly sleeved.
(iii) 6 Nos. 200 Amps MCCB outgoing along with 6 Nos. star delta starter for 79/75 kw chilled water & condenser water pump motor. (one standby)
(iv) 2 Nos. 400 Amps MCCB outgoing.
(v) 6 Nos. 32 Amps MCB outgoing along with 3 Nos. star delta starter for 9.5 kw motor.
| Page total c/o Summary |  |  |  | Rs
47 | Supplying, installing, testing and commissioning of main panel board cubical compartmentalised, floor mounted made of 2.0 mm thick steel sheet duly painted complete with voltmeter, ammeter, indicating lights for selector switch, incoming /outgoing feeders CTS contactors for remote control operation, complete all as specified fitted with following accessories. (For OT AHU) | Each | 1 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
(i) 1 No. 250 Amps MCCB incoming.
(ii) 1 Set 250 Amps MCCB TPN and neutral copper conductor bus bars duly sleeved.
(iii) 1 No. 200 Amps TPN MCB outgoing for 5x15 kw strip heater.
(iv) 1 No. 16 Amps TPN MCB outgoing for humidifire.
(v) 1 No. 63 Amps MCB outgoing along with 1 No. star delta starter for 22.0 kw motor.
48 | Supplying, installing, testing and commissioning of main panel board cubical compartmentalised, floor mounted made of 2.0 mm thick steel sheet duly painted complete with voltmeter, ammeter, indicating lights for selector switch, incoming/ outgoing feeders CTS contactors for remote control operation, complete all as specified fitted with following accessories. (For OT AHU). (i) 1 No. 100 Amps MCCB incoming. | each | 8 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
(ii) 1 Set 100 Amps MCCB TPN and neutral conductor bus bars duly sleeved.
(iii) 1 No. 100 Amps TPN MCCB outgoing for 40/35/25/20 kw strip heater.
(iv) 1 No. 32 Amps TPN MCCB outgoing along with 1 No. star delta starter for 11.0/7.5/5.5 kw motor.
(v) 1 No. 16 Amps MCB outgoing along for humidifire.
| Page total c/o Summary |  |  |  | Rs
49 | Supplying, installing, testing and commissioning of main panel board cubical compartmentalised, floor mounted made of 2.0 mm thick steel sheet duly painted complete with voltmeter, ammeter, indicating lights for selector switch, incoming/ outgoing feeders CTS contactors for remote control operation, complete all as specified fitted with following accessories. (For F.M. AHU's). (i) 1 No. 32 Amps MCCB incoming. | Each | 40 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
(ii) 1 No. 32 Amps MCCB outgoing along with 1 No. star delta starter for 11.5/7.5/5.5 kw motor.
50 | Supplying, installing, testing and commissioning of main panel board cubical compartmentalised, floor mounted made of 2.0 mm thick steel sheet duly painted complete with voltmeter, ammeter, indicating lights for selector switch, incoming/ outgoing feeders CTS contactors for remote control operation, complete all as specified fitted with following accessories. (For C.S. AHU's). (i) 1 No. 16 Amps MCB incoming. | Each | 14 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
(ii) 1 No. 16 Amps MCB outgoing along with 1 No. DOL starter for 3.7/2.2/1.1 kw motor.
51 | Supplying, installing, testing and commissioning of main panel board cubical compartmentalised, floor mounted made of 2.0 mm thick steel sheet duly painted complete with voltmeter, ammeter, indicating lights for selector switch, incoming / outgoing feeders CTS contactors for remote control operation, complete all as specified fitted with following accessories. (For scrubber). (i) 1 No. 100 Amps MCCB incoming. | Each | 1 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
(ii) 1 Set 100 Amps MCCB TPN and neutral conductor bus bars duly sleeved.
(iii) 1 No. 100 Amps TPN MCCB outgoing along with 1 No. star deta starter for 30 kw motor.
(iv) 1 No. 16 Amps MCB outgoing along with 1 No. DOL starter for 1.0 kw pump.
| Page total c/o Summary |  |  |  | Rs
52 | Supplying, installing, testing and commissioning of main panel board cubical compartmentalised, floor mounted made of 2.0 mm thick steel sheet duly painted complete with voltmeter, ammeter, indicating lights for selector switch, incoming / outgoing feeders CTS contactors for remote control operation, complete all as specified fitted with following accessories. (For Airwasher) | Each | 1 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
(i) 1 No. 63 Amps MCCB incoming.
(ii) 1 Set 63 Amps TPN and neutral conductor bus bars duly sleeved.
(iii) 1 No. 63 Amps TPN MCCB outgoing along with 1 No. star delta starter for 18.5/15.0 kw motor.
(iv) 1 No. 16 Amps TPN MCB outgoing along with 1 No. DOL starter for 1.0 kw pump.
Power Cabling
53 | Supplying and fixing PVC sheathed Aluminium cables with for various equipments through walls/ceiling/cable tray with appropriate clamps & fixing arrangements including M.S. perforated cable tray complete all as specified of
| (a) 31/2 C - 400 sqmm | RM | 200 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (b) 31/2 C - 240 sqmm | RM | 400 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (c) 4 C - 6 sqmm | RM | 430 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| Page total c/o Summary |  |  |  | Rs
| (d) 4 C - 4 sqmm | RM | 600 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
54 | Control Consol Supplying, fixing, testing and commissioning desk type control consol floor mounted paneled type fabricated from 2.0 mm CRCA sheet with indication lamp, ON/OFF/FAULT lamps alarm relays and internal wiring. | Each | 1 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
Control Cabling
55 | Supplying, fixing and terminations of multicore PVC control cabling of copper 1.5 sqmm upto control consol panel board through walls/ceiling/cable tray with appropriate clamps and fixing arrangements complete all as specified. | Job | 01 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
Earthing Conductor
56 | Double earthing continuity conductors of G.I. between panel boards and equipments as required of size.
| (a) 40 x 6 mm (Strip) | RM | 1400 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (b) 8 SWG (wire) | RM | 1600 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| (c) 10 SWG (wire) | RM | 1600 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| Page total c/o Summary |  |  |  | Rs
57 | Supplying and fixing rotational moulded polyethylene water storage tank (cylintrical vertical with closed top), hoised and fixed in position all as specified in SSR Part-I for 1000 litre capacity incl and providing brass float valve of suitable dia of inlet pipe with polythene float and fly nut complete screwed for iron pipe complete all as specified. Note : Tank to be hoised on roof of existing pump house building and all inlet, outlet, washout and over flow pipes shall be measured under respective parts of Sch 'A'. | Each | 01 | Rs ___________________ (Rupees _______________ ______________________) | Rs ___________
| Page total c/o Summary |  |  |  | Rs