## TENDER ETP
Ser No. | Description of Work | Unit | No of Units required | Unit Rate to be quoted by contractor in figures and words in Rs. | Amount
1 | 2 | 4 | 5 | 6 | 7
1 | Effluent Treatment Plant capacity 0.3MLD as per drawings and all as specified herein after :- (a) Diffused Aeration System. Construction, supply, installation of diffused aeration system complete with diffuser membranes made of EPDM rubber extruded membrane, with diffusers evenly spaced and adequately supported for equalization tank - 01 Job | Job | 1 | Rs ________________________ (Rupees ___________________ __________________________) | Rs _____________
(b) Effluent Transfer Pumps
Horizontal single stage open impeller suitable for solids upto 10 mm coupled to a horizontal TEFC electric motor and mounted on a MS fabricated base plate , with pressure gauge on each pump outlet, automatic duty switchover after each operation complete. Pump Capacity 8.33 lps (500 lpm) at 10 m head - 02 Set
(c) Tube settler with flash mixing Tank Self supporting ETP unit comprising of mixing tank for flash mixer, mixed solution tank and the main tube settler unit as per manufacturer’s design fabricated from 6 mm MS plates strengthened with MS structural members, painted inside with epoxy paint - 01 Set
| Page total c/o Summary |  |  |  | Rs
(d) Chemical Dosing Pumps Chemical dosing metering pumps mounted on 100 lit MSEP/PVC containers with lids complete with suction and delivery piping, injection assembly, complete with connection with solution making and storage tanks for continuous supply of chemicals. Dosing pump capacity as per manufacturer’s design. For Lime , Alum , poly-electrolyte and dosing for neutralization - 03 Set
(e) Solution making and storage tanks MSEP/HDPE self supporting solution making tanks each of 200 ltr capacity provided with water connection and agitation for proper mixing of the chemicals - 03 Set
(f) Flash Mixer Electrical vertical flash mixer for mixing and preparing dosing solution installed in the flash mixer tank on the ETP - 01 Set
(g) Sludge Transfer Pumps Horizontal, centrifugal type with TEFC electric motor and mounted on a MS fabricated base plate, with pressure gauge on each pump outlet, automatic duty switchover after each operation complete in all respects Pump Capacity 2 Cum/hour at 10 m head - 02 No
2 | WATER SOFTENING PLANT
| Supplying, installation, testing and commissioning of water softener fabricated from MS plate as per IS:2825 (shell & thick dished ends) complete with initial charge of resins. GI class 'C' face piping, CI butterfly valves, pressure gauge, hydraulic brine injector, accessories, painting inside with epoxy paint and outside with two coats of red oxide primer and two or more coats of synthetic enamel paint, regeneration capacity complete with resins of approved quality comprising of following parameters:- | Set | 1 | Rs ________________________ (Rupees ___________________ __________________________) | Rs _____________
| Page total c/o Summary |  |  |  | Rs
(a) Inlet (TDS) - 700-1000 PPM (Approx.)
(b) Inlet (Hardness) - 400-1000 PPM (Approx.)
(c) Outlet (Hardness) - Commercially Zero
Capacity - 55000 LPH (55 Cum/hour) Regeneration Period - 12 hrs. OBR - 550 Cum Operating Pressure - 3.0kg/Sq.cm Test pressure - 5.5 Kg/Sq.cm Suggested Resin Quantity - 8370 Lit. Suggested Height - 2600 mm Suggested dia - 2400 mm Brain Tank - 1 No. (100 lit. capacity)
3 | CENTRAL SEWAGE TREATMENT PLANT
| Supply, installation, testing & commissioning of Central Sewage Treatment Plant capacity 1MLD as per drawings and all as specified here in after :- | Each | 1 | Rs ________________________ (Rupees ___________________ __________________________) | Rs _____________
(a) Coarse Bar Screen Fabrication, Supply & Installation of coarse bar screen in MSEP of suitable size for 1.0 MLD and capable of holding particles upto 20 mm.- 02 Nos
(b) Fine Bar Screen Fabrication, Supply & Installation of fine bar screen in MSEP of suitable size for 1.0 MLD and capable of holding particles upto 6 mm.- 02 Nos
(c) Main Sewage Pumps Submersible single stage open impeller suitable for solids upto 40 mm size coupled to submersible electric motor complete with pressure gauge on each pump outlet complete with low level cut off, level controller to operate 2nd pump if 1st pump fails to meet the demand, automatic duty switch over after each operation in the STP.complete in all respects Pump Capacity 52 Cum per hour at 9 m head (Two working + one stand by)- 03 Nos
| Page total c/o Summary |  |  |  | Rs
(d) Air Blower for the FAB Reactor Electrically operated twin lobe air blowers and TEFC electric induction motor mounted on a common MS base plate with belt drive, belt protection guard, suction silencer and all accessories and supports. Blower capacity 500 cum/hr (each), 12.5 HP- 02 Nos
(e) Attached Growth bio reactor Manufacture, supply, installation of Attached Growth Bio Reactor (AGBR) suitable for 95% BOD removal efficiency, provided with PVC media, with specific surface area not less than 350 sq.m/cu.m . Media may be structured or floating type. The reactor should be complete with supports, as per specifications and as directed by GE. - 02 Nos
(f) Diffused aeration System Supply, installation of diffused aeration system complete with diffuser membranes made of EPDM rubber extruded membrane, with diffusers evenly spaced and adequately supported for following tanks. Pipe grid shall be separately measured as per piping rates, complete all as per specifications and as directed by GE.- 01 Set
i) Aeration units
ii) Main Equalization tank
iii) Sludge Holding Tank
iv) Treated Water Tank
(g) | Clarifier mechanism Manufacture, supply, installation, testing and commissioning of clarifier mechanism complete with scrapper mechanism for scrapping sludge at the bottom.- 01 Set
For Clarifier of main STP
(h) Main Filter MS fabricated /FRP multilayer filter vertical , pressure type dished ends fitted with internal distribution pipe on top, collector pipes and arms at bottom, inlet and outlet header complete with initial charge of filter media, face piping, accessories, working pressure 2.4 kg/sqcm ( Test pressure 3.75 kg/sq.cm. The vessel shall be painted with two coats of red oxide zinc chrome primer and two coats of paint. Capacity 60,000 liter per hour Filtarion velocity 10,000 liter per hour /sqm - 01 No
(i) Activated carbon filter
MS fabricated /FRP multilayer filter vertical , pressure type dished ends fitted with internal distribution pipe on top, collector pipes and arms at bottom, inlet and outlet header complete with initial charge of filter media, face piping, accessories, Working Pressure 2.4 kg/sqcm ( Test pressure 3.75 kg/sq.cm. The vessel shall be painted with two coats of red oxide zinc chrome primer and two coats of paint. Capacity 60,000liter per hour . Filtarion velocity. 10,000 liter per hour /sqm. - 01 No
(j) Chlorination Pumps Chemical dosing metering pumps mounted on 90 lit PVC containers with lids complete with suction and delivery piping, injection assembly, one set of buckets and containers for making solution for each pump complete in all respects. capacity as per manufacturer’s design. For Chlorine dosing of final effluent - 02 Nos.
(k) Instrumentation Magnetic type flow meter giving reading in liter per minute/liter per hour. (a) On Main STP inlet - 01 No
(b) Level Controllers - 03 No
Float type suitable to work in sewage water without cleaning
(l) Piping Supply, erection, jointing and testing MS pipes for waste water lines with necessary fittings, specials & supports as per technical specifications, etc. all pipes above ground shall be complete with two coats of red oxide zinc chrome primer and enamel paint , shade shall be as specified. - 01Job
(m) Valves Supply, Fixing and testing CI Butterfly valves for waste water lines with necessary fittings, specials & supports as per technical specifications, etc. complete all as specified and as directed by GE. - 01 Job
(n) Filter press Design, supply & installation of filter press in cast iron frame and polypropelene plates of size 24”x24” (min) with 32 plates with electric driven hydraulic power pack system complete in every respect required for efficient operation. - 01 Set
(o) Filter Press Feed Pumps Horizontal single stage open impeller suitable for solids upto 65 mm coupled to a horizontal TEFC electric motor and mounted on a MS fabricated base plate, with pressure gauge on each pump outlet, automatic duty switchover after each operation complete in all respects. Pump Capacity 5 Cum/hour at 10 m head - 01 Set
COLD STORAGE PLANT
4 | Supplying, instalation , testing and commissioning of pre fabricated cold storage plant electrically driven with suitable cooling/freezing units with control panel and all other accessories complete for temperature range minus 6 Deg C to 6 Deg C for 1.25 TR capacity details as under :- | Each | 1 | Rs ________________________ (Rupees ___________________ __________________________) | Rs _____________
(a) Room Dimension (Mt.) (2.39X2.39X2.4)
(b) Room Temperature (+) 4o C
(c) Ambient Temp. (45o C)
| Page total c/o Summary |  |  |  | Rs
(d) Material to be stored. (Pharma Products)
(e) Product Incoming Rate (300 Kgs/Day)
(f) Product Entry Temp. (20-22o C)
(g) Pull down time (12 hours)
(h) Insulation
(i) Walls and Ceiling (60 mm PUF with prepainted CRCA sheet).
(ii) Floor (60mm PUF Panels).
(j) Sliding Door size (0.9 x 1.9 m)
(k) Refrigeration unit (R-134A 15,000 BTUH (1.25 TR.)
5 | Supplying, instalation , testing and commissioning of pre fabricated cold storage plant electrically driven with suitable cooling / freezing units with control panel and all other accessories complete for temperature (+) 4o C for 5 TR capacity details as under :- | Each | 3 | Rs ________________________ (Rupees ___________________ __________________________) | Rs _____________
(a) Ambient Temp. (45o C)
(b) Material to be stored (F&V Products)
(c) Product Incoming Rate (1000 Kgs/Day)
(d) Product Entry Temp. (20-22o C)
(e) Pull down time ( 24 hours)
(f) Insulation
(i) Walls and Ceilling (60 mm PUF with Prepainted CRCA sheet as external finish and as intrnal finish)
(ii) Floor (60 mm PUF Panels)
(g) Sliding Door size (0.9 x 1.9 Meter)
(h) Refrigeration unit (R22 60,000 BTUH (5 TR.))
6 | Supplying, instalation , testing and commissioning of pre fabricated cold storage plant electrically driven with suitable cooling / freezing units with control panel and all other accessories complete for temperature range 2o C to 4o C for 4 body mortury cabinet details as under :- | Each | 01 | Rs ________________________ (Rupees ___________________ __________________________) | Rs _____________
(a) Dimension (mm) (2110x2400x1785 high)
(b) Interior finish (0.55 pre painted GI sheet)
| Page total c/o Summary |  |  |  | Rs
(c) Exterior finish (0.55 pre painted GI sheet)
(d) Front finish & trims ( 0.50 Stainless steel)
(e) Door & Door Frame - (FRP Door (45mm thk PUF)
(f) Foamed Panel
(i) Insulation thickness 80 (mm)
(ii) Insulation material (Rigid Polyurethane foam (CFC free), Denisity 40 Kg/m3)
(iii) Locking machanism (Cam-Locks embedded in foam)
(g) Standard Accessories
(i) Lamp (Vapor proof incandescent lamp, 40 W)
(ii) Temperature indicator cum controller (Electronic with Digital display)
(iii) Carriage assembly (Three piece, telescopic action, GI powder coated)
(iv) Mortuary Tray (One piece stain less steel tray with tubular edge and handles).
(h) Refrigerating system (Roof Top Mounting Unitary)
(i) Capacity (BTU/H) (6000)
(ii) Power supply (230 V/1 HP/50 HZ)
(iii) Compressor Power (KW) (1.25)
(iv) Total Unit Power Consumptions (KW) (1.75)
(v) Operating conditions ( 4 Deg C Room Temperature @ 35 Deg C Ambient)
(vi) Over all Dimensions (mm) of Ref. Unit (1140 (L) x 900 (W)x 415 (H))
Note : Cables for electric connections to the equipments mentioned above shall be measured under respective items of Sch 'A' Part-XII.
7 | Supply, installation, testing and commissioning of LT panel board for effluent treatment plant, out door type, cubical, floor mounted, factory made, totally enclosed, made out of CRCA sheet not less than 16 SWG mounted on angle iron 50x50x6 mm with MS plate suitable for bottom cable entries with cable glands of brass of suitable size weather proof with front and back open including adjustable type locking arrangement and powder coated painted internally and externally providing and consisting of the following fitments/accessories :- | Each | 01 | Rs ________________________ (Rupees ___________________ __________________________) | Rs _____________
(a) Bus bar chamber 3 phase, 4 wire, 440 volts, 50c/s consisting of copper bus bar of capacity 100 Amps (all the four bus bar to be of the same size including neutral) for incoming/outgoing feeder and fixing on insulators with PVC coloured sleeves - 01 Set.
(b) MCCB, 4 pole, 63 Amp, 415 volts, 25 KA (Ics) - 01 No. (incoming).
(c) MCCB, 4 pole, 25 Amp, 415 volts, 10 KA (Ics) - 01 No. (outgoing).
(d) MCB DP 25 Amps, 230 volts, 10 KA (Ics) - 03 Nos.
(e) MCB DP 16 Amps, 230 volts, 10 KA (Ics) - 03 Nos.
(f) DOL starter for upto 3 HP motor - 04 Nos.
(g) Ampere meter 0-100 Amps, square mounted, 96 mm square, with CTS 100/5 Amp rating with selector switch electronic type - 01 No.
(h) Voltmeter 0-500 volts square mounted, 96mm square with selector switch electronic type - 01 No.
(j) Internal wiring connection in colour coding with suitable copper cable/lugs with end terminal - 01 Job.
(k) Indicator lamp LED type in RBY colour set of 3 - 01 Set.
| Page total c/o Summary |  |  |  | Rs
8 | Supply, installation, testing and commissioning of LT panel board for sewage treatment plant, out door type, cubical, floor mounted, factory made, totally enclosed, made out of CRCA sheet not less than 16 SWG mounted on angle iron 50x50x6 mm with MS plate suitable for bottom cable entries with cable glands of brass of suitable size weather proof with front and back open including adjustable type locking arrangement and powder coated painted internally and externally providing and consisting of the following fitments/accessories :- | Each | 01 | Rs ________________________ (Rupees ___________________ __________________________) | Rs _____________
(a) Bus bar chamber 3 phase, 4 wire, 440 volts, 50c/s consisting of copper bus bar of capacity 250 Amps (all the four bus bar to be of the same size including neutral) for incoming/outgoing feeder and fixing on insulators with PVC coloured sleeves - 01 Set.
(b) MCCB, 4 pole, 200 Amp, 415 volts, 25 KA (Ics) - 01 No. (incoming).
(c) MCCB, 4 pole, 40 Amp, 415 volts, 10 KA (Ics) - 03 No. (outgoing).
(d) MCCB, 4 pole, 63 Amp, 415 volts, 10 KA (Ics) - 02 No. (outgoing).
(e) MCB DP 25 Amps, 230 volts, 10 KA (Ics) - 04 Nos.
(f) DOL starter for upto 6 HP motor - 04 Nos.
(g) Star Delta starter for 12.5 HP motor - 02 Nos.
(h) Ampere meter 0-100 Amps, square mounted, 96 mm square, with CTS 100/5 Amp rating with selector switch electronic type - 01 No.
(j) Voltmeter 0-500 volts square mounted, 96mm square with selector switch electronic type - 01 No.
(k) Internal wiring connection in colour coding with suitable copper cable/lugs with end terminal - 01 Job.
(l) Indicator lamp LED type in RBY colour set of 3 - 01 Set.
| Page total c/o Summary |  |  |  | Rs